[image: image1.jpg]



Pipe2016
Examples Manual
Demonstration Examples
Class Exercises
Training Exercises
Case Studies
Campus Facilities

New Surge Demo Files
September 2013
LICENSE AGREEMENT
This is a legal agreement between the user and KYPipe LLC. By accepting, using or installing any portion of this software the user agrees to be bound by the terms of this agreement.
SOFTWARE LICENSE
GRANT OF LICENSE: For each license purchased from KYPipe, LLC, or one of its authorized distributors, KYPipe LLC grants to the user the right to use one copy of the software program(s) on a single terminal connected to a single computer (i.e., with a single CPU). The user may not network non-network versions of the software or otherwise use single user versions on more than one computer terminal at the same time. Network versions are only to be used with one physical site (buildings at the same mailing address) and are not to be used in a WAN environment. WAN licenses may be used only for the number of sites licensed.  The number of network licenses purchased for a network version is the maximum number of users permitted to run the software concurrently. If granted for an evaluation period by KYPipe LLC, user agrees not to use the software beyond the evaluation period specified by KYPipe LLC. The user agrees not to utilize features, options, or number of pipes beyond the license the user has purchased.
COPYRIGHT: The software and the documentation are owned by KYPipe LLC and are protected by United States copyright law and international treaty provisions. The user must treat the software like any other copyrighted material except that the user may make one copy of the software solely for backup or archival purposes or may transfer the software to a single hard disk and keep the original disk(s) sole for backup or archival purposes. The user may not copy the written materials accompanying the software without explicit written permission from KYPipe, LLC.
TRANSFER BY USER: The user may not rent, lease, assign or permit others to use the software but may transfer the software and accompanying materials on a permanent basis provided the user retains no copies and the recipient agrees to the terms of this agreement. As a condition to permit the recipient use the software under this License Agreement, when such a transfer is made, KYPipe, LLC must be notified, in writing, of the transfer, including the identity and address of the recipient, and the agreement of the recipient to the terms of this License Agreement. 
OTHER RESTRICTIONS: The user may not modify the software. The user may not reverse engineer, decompile, disassemble, or otherwise attempt to determine the source code of the software. The user shall protect the software from unauthorized use, and shall protect the software and the intellectual property from infringement by others. The user shall notify KYPipe, LLC, in writing, immediately upon receiving any information that would indicate that the software is being used in an unauthorized manner or the intellectual property is being infringed.
DISCLAIMER
Although every reasonable effort has been made to ensure that the results obtained are correct, neither the author(s) nor KYPipe, LLC assumes any responsibility for any results or any use made of the results obtained with these programs. THE SOFTWARE IS SOLD AS IS WITH NO IMPLIED WARRANTIES, INCLUDING WARRANTIES OF MERCHANTABILITY AND FITNESS FOR ANY PARTICULAR PURPOSE. NO EXPRESS WARRANTY EXISTS EXCEPT AS SPECIFICALLY SET FORTH IN WRITING BY KYPIPE, LLC. IN NO EVENT, REGARDLESS OF THE NATURE OF ANY CLAIM, WILL KYPIPE, LLC, ITS MEMBERS OR AFFILIATES, BE LIABLE FOR ANY LOSS FOR PERSONAL INJURY, BUSINESS INTERRUPTION, LOST PROFITS, OR INCIDENTAL OR CONSEQUENTIAL DAMAGES, AND ITS LIABILITY, IF ANY, SHALL BE LIMITED TO THE PURCHASE PRICE OF THE SOFTWARE.
USE OF THE DOCUMENTATION AND PROGRAM
The documentation is provided for the use of individuals or companies which purchase it from KYPipe, LLC. Except for back-up copies, the program disks or documentation may not be copied, marketed, or distributed without explicit written permission from KYPipe, LLC. For users who wish to use the programs on networks or multiple computers or different locations, network copies and multiple copy discounts may be obtained. Please contact KYPipe, LLC for details. 
GOVERNING LAW AND VENUE FOR ENFORCEMENT AND DISPUTES
This Agreement will be governed by and construed in accordance with the substantive laws of the Commonwealth of Kentucky, and, to the extent federal law applies, to the laws of the United States. The state and federal courts of Fayette County, Kentucky, shall have exclusive jurisdiction over any claim brought against KYPipe, LLC, and the user agrees to submit to the jurisdiction of the state and federal courts of Fayette County, Kentucky, in the event any claim is brought against the user, and user waives all defenses to jurisdiction and inconvenience of forum.
How to Use the Examples Manual

This manual is an excellent resource for a wide range of modeling activities.  There are examples for absolute beginners (see Section 2 – Class Exercise 1 – QuickStart Example), for design scenarios (Section 3 – Training Exercises – Pumping Stations and Pumping Costs), for special applications (See Campus Facilities), and for a wide range of transient scenarios (See Section 1 – Surge Demonstrations).
Each example narrative is accompanied by a pre-prepared model file.  The names of the files are noted in each section.  The model files are located in the default file folders installed with the software.  A folder exists for each Section of this Examples Manual as follows:
KYPipe Docs

Examples Manual


1 Demonstration Examples



KYPipe Demonstrations



Surge Demonstrations


2 Class Exercises 1


3 Class Exercises 2


4 Training Exercises


5 Case Studies


6 Campus Facilities



7 Surge Demos

Contents
6Section 1 – Demonstration Examples


6Pipe2016: KYPipe Demonstrations and Example Data


7Demo1 – Municipal Water Distribution System


71-1 Demo1 –Description of System


101-2  Demo1 – Developing the Pipe2016 Model


141-3 Demo1 – Regular Simulations and Changes (Demo Model.P2K)


221-4 Demo1-2 – Additional Node Types (Demo Other Nodes.p2k)


281-5 Demo1-3 – Fire Hydrants (Demo Hydrant Analysis.P2K)


311-6  Demo1-4 – EPS (Demo EPS.P2K)


361-6  Demo1-5 – EPS (Demo EPS Control Switch.P2K)


381-6  Demo1-6 - Water Quality Simulation (Demo Water Quality.P2K)


421-6  Demo1-7 - Optimized Calibration (Demo Calibration.P2K)


46Surge Demonstrations and Example Data Files


47I.   Demo1 – Municipal Water Distribution System


491  Pump Rundowns Using Pump Head/Flow Table (Pump Run Down.P2K)


562  Pump Trip Using Pump File (File Pump.P2K)


643   Pump Startups Using Pump File (Pump Startup.P2K)


674  Fixed and Modulating Regulating Valves (Regulator.P2K)


776  Valve Closures (Altitude Valve.P2K)


807  Relief Valve to Control Pressure Surge Due to Valve Closure (Pressure Relief Valve.P2K)


838  Hydrant Operations (Startup and Shut Down) (Hydrant Open.P2K


889  Simulated Line Break Using Rupture Disk (Rupture Disk.P2K)


9110  Simulated Pump Trip Using Inflow Node (Negative Demand.p2k)


94Appendix 1-A   Demo1 – Municipal Water Distribution System


96Demo1 -  Pipe and Node Data


97Section 2 - Class Exercises


97Class Exercise 1 - Quick Start Example (Quickstart1.p2k)


97Step 1  -  Initial Preparation


97Step 2 - System Layout


99Step 3  -  Analyze System and Review Results


101Step  4  -  Some Additional Simulations (Quickstart2.p2k)


104QuickStart Example 2 – SI Units


116Class Exercise 2 – Water Distribution System (Example Base.P2K)


116Description


119Results


120Extended Period Simulations (EPS) (example eps 24-hour.p2k, 2 and 3)


124Surge Exercises


124Surge 1 Setup (example surge rapid shutdown.p2k)


128Surge 1 Results


129Surge2 Setup (example surge compressor tank.p2k)


130Surge2 Results


130Sizing Bladder Tank


132Water Quality Exercises


132WQ1 (Water Age in Tank 25%.P2K):


134WQ2 (Water Age in Tank 75%.P2K):


135WQ3 (Water Quality Chlorine.P2K):


137WQ4 (Water Quality Trace.P2K):


139Section 3 – Training Exercises


139Training Exercise #1 – Industrial Water Distribution System


140Creating the Model


140Model Data


143Regular Analysis Results (Industrial Base.P2K)


144Using Change Data


146Results for Multiple Simulations (Industrial Changes.P2K)


146Training Exercise #1 – Extended Period Simulations (EPS)


146EPS1 (Industrial EPS1.P2K)


147EPS2 (Industrial EPS2.P2K)


147EPS Data


147EPS Results


151Training Exercise #1 – Surge Analysis (Industrial Surge.p2k)


151Problem description


152Surge Model Setup


154Results


154Using the Pipe2016 : Surge Option for Cavitation Calculations


1562) Surge Analysis - Modulating Regulating Valves – Training Exercise #1


160Training Exercise #2 – Pump Stations and Pumping Costs (pump design.p2k)


160System Description


161Additional analysis (pump design 2.p2k)


161Setting up the Model


161Solutions


164Training Exercise #3 – Hydraulic Analysis of Sprinkler System


164System Description (Demo Fire Sprinkers.P2K)


164Additional analysis


166Setting up the Model


167Analysis Results


169Section 4 - Case Studies


169Case Study #1 - Landfill Gas Extraction Piping System (Landfill Gas Extraction.P2K)


169Description


169Model Data


173Results


175Case Study #2   Modeling Air/vacuum Valves with Surge (Air Vacuum Valves.P2K)


179Campus Pipe Distribution Facilities Modeling


1801)  Potable Water Distribution Model (Campus Potable Water.P2K)


1862)  Chilled Water Model (Campus Chilled Water.P2K)


1893)  Hot Water Model  (HotWater.P2K)


1944) Natural Gas (methane) Distribution (Campus Gas Distribution.P2K)


1985)  Saturated Steam Distribution System (Campus Steam Distribution.P2K)


2026)  Superheated Steam Distribution Model (Campus Superheated Steam.P2K)


207Pipe2016: Surge Demo Examples and Files


2081)
Uncontrolled and Controlled Pump Shutdown


2132)
Uncontrolled and controlled pump startup


2153)
Surge Protection (surge tank) for uncontrolled pump shutdown


2164)
Pump trip using full pump characteristics (pump file)




Section 1 – Demonstration Examples
Pipe2016: KYPipe Demonstrations and Example Data
Demo1 – Municipal Water Distribution System
A simple pipe system representing the main pipes of a small municipal distribution system is shown in Figure 1-1.  This system is used to demonstrate the use of Pipe2016: KYPipe for regular and extended period simulations and Pipe2016: Surge for surge analysis.  A number of modeling features are demonstrated with the data files provided in the Examples folder (“Examples” button in the File Open menu). In this manual the data along with additional details are provided so the user can lay out and set up these examples. A number of additional exercises are presented to illustrate Pipe2016 modeling elements and features.

[image: image2.png]2N
A
@%VQ QOQQ o
SN

0
% V%% 0 @O
’5 <7 QQ
A OQQ v
Q{





Figure 1-1 Pipe System – Demo1

1-1 Demo1 –Description of System
The system is supplied by a pump which has the following head/flow/efficiency data:

                                                     [image: image3.png]Head| Flow Eff%
0 e
200 B00 77
160 1200 70





The system has 2 overhead 35 foot diameter storage tanks with the following characteristics:

Tank 1:  Max. elevation = 755 ft., Min elevation = 735 ft. Initial level = 750 ft.

Tank 2:  Max. elevation = 755 ft., Min elevation = 730 ft. Initial level = 749 ft.

The pipes are 6, 8, and 10-inch ductile iron as shown below and the Hazen Williams Roughness coefficients are all 130. The pump suction and discharge lines are 12 inch ductile iron.
[image: image4.png]



Figure 1-2 Pipe System Diameters - Demo1
The node elevations and demands (in gpm) are shown in the figures below.

[image: image5.png]


                   

                                   [image: image6.png]\




   

Figure 1-3 Pipe System Elevations and Demands - Demo1
1-2  Demo1 – Developing the Pipe2016 Model
Step 1 – Background Map -  Ideally you will have a scaled background map which can be imported into Pipe2016 and used to lay out the pipes and automatically scale the pipe lengths. If available this map should be imported to use as the background for the pipe system. For this example the background map shown in Figures 1-1 to 1-3 is a .dwg file which is a scaled vector drawing file. This map is called City.dwg and may be found by clicking the Add Demo Map button in the Backgrounds menu shown below.  The map is imported as a background map as shown in Figure 1-4a and 1-4b. 
KYnetic Background menu icon: [image: image7.png]



Classic tabs:

 [image: image8.png]Map | Map Settings ISyslem Data| Of

Colors/Sizes |Backgrounds | Grids | Lz

Background Files | intemet Maps |




            [image: image9.png]AddMap | AddDemoMap | Remove Map Scale Background to Pipes

Propeties Scale Pipes to Background

City.dwg visible] Make Map Visible/Hidden

Zoom to All Maps.
Zoom to Maps and Pipes

‘Start MapLink Utiity

Xshit [0 Yshit [0 Scale Factor [1
¥ Show Text on DXF and DWG maps (slower)





Figure 1-4a Adding the Background Map - Demo1

[image: image10.png]O selectamap el 11

.5

faa it

canwashbmp  ce2map.bmp.

Lo [ 1 mages i

r

CTYDWG

=

Fiename:  [CTY.DWG

Fiesof type:  [Map Fies - Al Types.

\Li
e |





Figure 1-4b  Adding the Background Map - Demo1
Step 2 – System Layout -  Using the mouse and the background map as a guide the pipe system layout can be developed very quickly. Once the pipe layout is complete the two tanks, supply reservoir and pump nodes can be created by selecting the locations and using the Node Type dropdown list to designate the node type. At this point the pipe system will appear as shown below in Figure 1-5

[image: image11.png]



Figure 1-5 Pipe System Layout – Demo1

Step 3 – Provide Pipe Data - The recommended means to provide pipe data is to first develop the Pipe Type Table. This is accessed through the KYnetic Components menu icon [image: image12.png]


 or the Classic tabs Setup/Defaults | Pipe Type.   The following table is appropriate for this example. The Estimated 10 Year Roughness is utilized with the Pipe2016 aging feature and is optional.

[image: image13.png]Material | Rating [Nominal Diameter Actual Diameter [Unit Cost Reference Roughness  Estimated 10yr Roughness
1 b 150 6 130 113
2 150 i 130 120
3 d 150 10 130 121
4 i 150 12 130 122




Figure 1-6  Pipe Type Table – Demo1

[image: image14.png]Select Pipe Type

Update Listto Include all Pipe Types Cancel

- 150-5
i~ 150°8
di-150-10
di-150-12




Figure 1-7 Pipe Type Table – Demo1

Figure 1-7 illustrates the Pipe Type data entry. When the pipe is selected in the map and Pipe Type is clicked the menu shown above appears. A click on the second entry (di-150-8) will result in all the data items except Length being entered into the pipe data box. The length has been scaled using the background map so only the entry for Pipe Type is needed to provide the required pipe data.  Additional data for Fittings or other Pipe2016 features may be entered but this is optional. The Pipe Type is entered for each pipe to complete the data requirements for pipes.

Step 4 – Provide Node Data -  Data is then entered for each node in the system.  The data requirements vary depending on the Node Type. Node data entry is illustrated below for the top center junction, the pump and Tank 2.

[image: image15.png]Narne[[5
dunction -

Elevation 613

T —

Dernand 45
—_—

D Typefi ~




[image: image16.png]unction Single Der

Name. 3
Elevation 613
Demand 5
Demand Type 1





Junction Node: Classic – KYnetic

[image: image17.png]¥ Fixed Diamster

Diameter 35




[image: image18.png]730

49

0

North Tank
3




Tank (Fixed Diameter):  Classic - KYnetic

[image: image19.png]Name[Pump-1 =
[Furo ~||| Head| Flow Ef%

Elevation 610 08
e |[200 [so0 77

Sp Ratio! 1601200 70
——r—— o o o
o 0 o

o 0 o

o 0 o

oo T o 0 o
ump Type b o o
@ Table © File |||y
© Const” Rated |2 0 0
<«|Froe oo o




[image: image20.png]Pump - Table

Name. Pump-1

Elevation 610
Pr
Parallel Single i‘ Head

(Check Valve X Head Flow Effienc





Pump (Table):  Classic – KYnetic
Figures 1-8 Node Data – Demo1

1-3 Demo1 – Regular Simulations and Changes (Demo Model.P2K)
Step 1 – Check the Data and Run the Analysis -  Once data entry is complete various data checks should be performed.  A graphical data check is very useful and is performed by turning on labels such as Node Elevation and Pipe Diameter and Roughness as shown in Figure 1-9. 
[image: image21.png]Pipe diameter and roughness
Pipe material and rating

Pipe fittings

Pipe results

Peak velocity

Selected pipe labels

Pipe labels off

Node name
Node title

Node clevation

Junction demand and type
Node results




    [image: image22.png]e Pipe2014 [demo model]
(€]

—

Node Labels

s/min]
rs/min]

J-5|
©





Labels menu – Node Elevations:  Classic - KYnetic
[image: image23.png]Sy O@@





Figure 1-9 Graphically Checking Data – Demo1-1

[image: image24.jpg]Conttours

Conmectivity Check
Find/Purge Paralel Pipes
0CS Screen (analysis)
Analysis
Summary/Supply Plot

Calbration Wizard
Undo Calbration



[image: image25.png]Information ]

£)) o Errors

&




     [image: image26.jpg]Error Check
Connectivity Check
Find/Purge Parall Pipes

OCS Screen (Analysis)

Summary/Supply Plot:
Inventory/Cost
Power Cost
profie
Skeletonize
Calibration Wizard
Undo Calibration




Classic
[image: image27.png]By Pipe2014 [demo model]

©|gs 6= P = R
ater Quality Skeletonize Error Check Analyze
s | | _ s o |
Quaty Catraton | | Excludefincude | | FindPurge Paralel | ocs

Connectivity Check




KYnetic
Figure 1-10 Error Check and Analysis Data – Demo1-1

Once the data is reviewed an Error Check should be performed as shown in Figure 1-10.  Then an Analysis can be carried out as shown also in Figure 1-10. The analysis will be for the Baseline Conditions described by the input data.  The results for pressures at nodes are shown in Figure 1-11.
[image: image28.png]



Figure 1-11 Node Pressures for Baseline Data – Demo1-1

[image: image29.png]"

w o @

AQ A

S L

\@0 o
¥




 

Figure 1-12 Pipe Flows (gpm) for Baseline Data – Demo1-1

Step 2 – Add Change Data and Run Additional Simulations -  It is desired to set up the following three scenarios:
Case 0 - The pump is running with normal (Baseline) demands
Case 1 - The pump is off and the tanks supply the system
Case 2 - The pump is off and a fire demand of 650 gpm is placed at Junction J-13

The first simulation (Case 0) is always the Baseline Data and is the analysis illustrated in Section 3-1 Step 1.  The additional cases may be run by modifying the Baseline data and re-running the analysis.  However, Pipe2016 has the capability to run multiple simulations by specifying Changes to various Pipe and Node parameters, allowing the Baseline Data to remain the unchanged. One advantage of this approach is that the results for the various cases are easily compared in Tables and Graphs.

The Change Data screens used to set up these 2 additional simulations are shown in Figure 1-12.  These are accessed by clicking on the node in the map screen and selecting the [image: image30.png]<]



 icon at the bottom of the Node Info window (KYnetic) or the ‘Chng’ (Change) button at the top of the node information window (Classic).  To set up an additional case just select the node(s) and/or pipe(s) and enter the desired case number, parameter type (click center column and select from list) and the new parameter value. 

[image: image31.png]Node Changes

] o

Time/.
Case

1 [C[Close | &

Value




 [image: image32.png]Changes for Pump-1

[change

[Valie

Closed

Chose.




Case 1:  Classic - KYnetic

[image: image33.png]Node Changes

o] oo

Time/.
Case

2 Deso (A

Value



[image: image34.png]Changes for J-13

[change

[Valie

Demand

%0




Case 2:  Classic - KYnetic
Figure 1-13 Change Data for Cases 1 and 2 – Demo1-1

[image: image35.png]A
g : v
u.?s(@@@@@
{ ) N
@ 4_ \
RIS \s
R A <
/Fe« S «'(\g< T
S
Shar
oS U o
LR R
s Vol
e

£





Figure 1-14 Node Pressures for Case 1, Pump off – Demo1-1

[image: image36.png]( \} Q\
\ . /(ggo \
m~ R Y

oauls ey
LN OISO
D_";{»i ' ﬁ\D%/(\ . QU

Al wi
=LA CDownthy





Figure 1-15a Node Pressures for Case 2, Pump Off, Demand 650 gpm – Demo1-1

Pressure contours are an effective alternate way to present results. Figure 1-15b shows the setup screens and the resulting pressure contour plot for Case 2. 

[image: image37.jpg]=

| | i | |
Nods Contours/Emphasis | Pipe Emphasis |
Node Emphaslleontours

Walue Caol Crlanp Show Contours [ Show Emphasis
T o _ ™ Pump Status [ L ahel Contours ¥ Show Key
2 | | Auto Fill Parameter Key Locatio
4k _RangeFil | Contour Style LabeliKey Font Size

F 4




Classic Contours menu

[image: image38.png]= IZ(I ”; 2 f @ iﬁg Pipe2014 [demomodel] Case2  @[%[ |||

lﬂ Values/Colors Key Pf S = 't. 2_9 1
ﬂ E B o - P“”mmmeu::;L ;phasls Transparency Contour Pattern x
M E e e NESE

o =l ml 1 rrr—= sny L) HEE e





KYnetic Contours menu
[image: image39.png]



Figure 1-15b Node Pressures Contours for Case 2 – Demo1-1

1-4 Demo1-2 – Additional Node Types (Demo Other Nodes.p2k) 
[image: image40.png]



Figure 1-16 Additional Node Types  – Demo1-2

A number of additional Node Types are illustrated in this example. These include:

a) Active Valve

b) Regulator

c) Loss Element

d) Sprinkler

For items a, b, and c insert a node at the indicated location.  To Insert click on pipe at the intended location and select Insert icon [image: image41.png]


 (bottom of Pipe Info window in KYnetic) or “Insrt” button (top left of Pipe Information window in Classic).  Then select the node type from the drop-down list.

The Active Valve is a pump control valve located just downstream from the pump. It is a 10 inch Butterfly valve with a Cv = 1000 when fully opened. Note that an Active Valve can be characterized by the wide open Flow Coefficient (Cv100%) or the wide open Resistance (R100%).   A check box in the Preferences menu [image: image42.png]


 (KYnetic) or System Data | Preferences (Classic) is available to switch from one description to the other (as shown in Figure 1-17). The data boxes for this Active Valve are shown in Figure 1-17.

[image: image43.png]


[image: image44.png]Name|ay-1
[Active Vale |

Elevation 510

Cv 100%1000

Init Ratio|!
iRatia]___

Valve Type

=




[image: image45.png]



[image: image46.png]¥ Use Valve Coeficient (Cv) instead
of Resistance (R) for Active Valves




Figure 1-17  Active Valve Data  – Demo1-2:  Classic - KYnetic
A Flow Control Valve is located in the pipe leading to Tank 2 to limit the flow to 300 gpm. The setup for this element is shown in Figure 1-18. In addition a Backflow Preventor located in the pipe leading to J-2 on the lower left side in the pipe system. This device has head loss vs. flow data and uses a curve based on this data to determine the loss through the element. The data for these elements is shown in Figure 1-18
[image: image47.png]Name[Rv-1

Regulator  ~|

Elevation 613

Setiing 00

Regulator Type
Fev-1 <]

|



  [image: image48.png]



Flow Control Regulator:  Classic – KYnetic

  [image: image49.png]Name|[-1 o =

[Loss Etement  ~||| Head| Flow Ef%

Elevation|517 ‘7” 0
e —

25 70 0
35 [0

0 0 o



[image: image50.png]Loss Element




[image: image51.png]Head Flow





Loss Element:  Classic – KYnetic
Figure 1-18 Regulator and Loss Element Data – Demo1-2
                      [image: image52.png]


        [image: image53.png]Name[S1
Sprinkler/Leak

Elevation

Constant |

Length|4
—_
Diameter/2
e
Elev Chal4
e
Elbows

—




[image: image54.png]Sprinkler/Leak
s1

185

-





Sprinkler Data:  Classic - KYnetic

[image: image55.png]Name [P-25

Pipe Type

Diam

Myl |di

Ring [0 <

Lengthjoon @ F

Roughfia0 @ F

Fittings |1~ Closed



[image: image56.png]



Additional Pipe Data:  Classic - KYnetic
Figure 1-19 Additional Pipe and Sprinkler Data – Demo1-2
For item d select the existing node and move the mouse to the location of the sprinkler and RC. Then select the new node and change it to a sprinkler. A 900 foot long 4 inch line leading to a 1 inch sprinkler (orifice) was added to model a fountain. At the fountain a 4 foot long 2 inch pipe rises 4 feet to the sprinkler orifice. The data for the additional pipe and sprinkler are shown in Figure 1-19.  Data for the pipe connecting a sprinkler is included with the sprinkler data. The Sprinkler Constant can be obtained using the Sprinkler/Blowoff Constant Tool as shown below.
KYnetic Tools menu icon:  [image: image57.png]



           [image: image58.png]10 Year H Coefficient
i Slam Pressure Surge.
airvalve Orfice Size

Bladder Precharge

Caleuator

Force Calculations

Gas Properties

Generate Intermediate Pup Fil
Hase and Nozzle Constants
Inertis/speciic Speed
Modusting (Regulating) Valve:
Power (HP or kW) Calcultions
Profie Import

Pump File Characteristics
Residual Pressure Adjustment
Resistance Calculations

Select Pump File

Spike Track

Units Convertor
Valve stroking
Wave Speed



             [image: image59.png]. Pipe2000 - Sprinkler/Blowoff C.

Uit [Engish

Compude Based on [Gice dameter
Dismterof Oz [;——— in
DisneterciPpes
Discharge Cosficint [§52 — Suggest
Specic ravty [T

Spinkler Constart KS[75.476

[Ke=0/(@ 0] where Ks f spikler corstant,
[0 fowate in gpm {or /5] and dP i pressure
o i psi or kPa)





Figure 1-20  Sprinkler/Blowoff Constant Tool  – Demo1-2
[image: image60.png]AR RN
g@ V@%%

&

\ A

)
SR GOSOEN M
A“Q. QQO Vi

AN Q? O
SR el o





Figure 1-21a Flowrates (gpm) – Demo1-2
Figure 1-21a and 1-21b show the pressures and flows obtained by the hydraulic analysis which includes the additional elements. The Tabulated Report contains additional sections summarizing results for various elements. The dropdown list illustrated below may be accessed when [image: image61.png]


 (KYnetic) or Report tab (Classic) is selected. Figure 1-22 shows the report generated for Pumps and Regulators.
[image: image62.png]Purnp Report

(A
Data Sumrmary
Case: D

o R
Tank Report

RV Report
Constraint Report

T





[image: image63.png]o @
b

;
I

//
%
Q

2

e
SO

N

Q&

i





Figure 1-21b  Pressures (psi)  Demo1-2
[image: image64.png]PUNP/LOSS ELENENT RESULTS

INLET  OUTLET ~PUMP EFFIC- USEFUL INCRENTL TOTAL #PUNPS #PUNPS NPSH

NAME  FLOVRATE HELD HELD  HEAD  ENCY  POVER COST  COST PARRLLEL SERIES Avail.
(grpm) (£e) [F T ] (Hp] (5 ) (£e)

L-1 75.00  132.49  105.96 -26.5 = o 165.7
Pump-1  1105.50 -2.04  165.28  167.3 = w30




[image: image65.png]REGULATING VALVE REPORT

VILVE  VALVE  VALVE  VALVE UPSTREAN DOWNSTRERH THROUGH
(psi or gpm) (psi) (psi)  (gpm)

RV-1  FCV-1 300.00 ACTIVATED  §9.38 s9.01 300.00




Figure 1-22  Pump and Regulator Reports -  Demo1-2
1-5 Demo1-3 – Fire Hydrants (Demo Hydrant Analysis.P2K)
Locations and reference names are shown below (Figure 1-23) for 9 fire hydrants.  Fire flow test data for the hydrants is shown in Figure 1-24. To Insert these hydrants, click on pipe at the appropriate location and select Insert icon [image: image66.png]


 (bottom of Pipe Info window in KYnetic) or “Insrt” button (top left of Pipe Information window in Classic).  Then select Hydrant from the drop-down list.
[image: image67.png]



Figure 1-23  Fire Hydrant Locations  Demo1-3

              [image: image68.png]


[image: image69.png]Elv.
611
612
610
620
610
615
605
605
815

Static Pressure Residual Pressure Residual Flow

66
58
59
54
65
63
7
70
58

47
a4
34/
45
Gl
a4
60
58
7]

800
370
660

1400

1550
370

1700

1330
407




Figure 1-24 Fire Hydrant Test Data - Demo1-3
[image: image70.png]Narme[H-1
Hydrant ~|

Elevation |11
—

St Prs |8
—_—
Rsdl Prs 47
—_—

250l Flow|300
——

Graph
Measured Data




 [image: image71.png]Elevation

Title

Static Pressure

66

Residual Pressure.

Residual Flow

Calculated St Press 52 7

Calculated Firefiow

1718.09





Hydrant Data:  Classic – KYnetic

[image: image72.png](Q)EEDEL PR R EE

tory / Costs Break / Intrusion Hydrants / Flushing

comentory || smiscpporeas || rusninganayss |

y sekectedtens || pipe BreakReport | Fushing Report_|

wercost || msonatpoi || _Anatze ydran Fiws |
Intruison in Polygon Hydrant Report
Intrusion Report Hydrant Graph.




[image: image73.png]Hydrar Test Graph

Pressure

0
i3
1m0

—a—H1 12003 @20

1250





Figure 1-25 Fire Hydrant (Test) Data and Flow Plot -  Demo1-3
Once a hydrant is added the hydrant can be selected and the elevation and fire flow data shown in Figure 1-26 can be entered as shown above (for reference and graphing only, not used for calculation). The Graph button or the KYnetic menu shown above allows you to generate Fire Flow Test Data plots such as the one shown in Figure 1-25. This plot using a Q 1.85 factor for the X axis is used for predicting the available fire flow from the test data (this follows AWWA and NFPA guidelines). Hydrants also allow you to use a model to calculate available fire flows. The Pipe2016 setup screen for Fire Flow calculations is shown below in Figure 1-26. Pipe2016 provides a variety of fire flow and hydrant flushing calculations although the most common is the Available Fire Flow at a Specified pressure (usually 20 psi) which is illustrated below.

[image: image74.png]Analysis Type

Analysis Year © KyPipe € Flushing Planner
I~ Use Current Year, © Water Quality (EPANET) " Locate Remote Sprinkler Area.
2026 € Hydraulic Calibration € Water Quality Calibration
€ Rural Analysis © Temperature Dependent Liguid
Analyze
- @ Fireflow and Hydrant Analysis © Required Capacity (Sprinklers)
Canczl € System Head Curves

W SortNumerically (slower)
I™ Save System Before Analysis

Load [every =] setofresutts.  Load alltimes ¥
Fireflow with specified min pressure Minirmum Pressure for Fireflows [20

Stetic Pressure Limit [0 (nodes with static pressure below this value will be ignored)

Fireflow Nodes

 Selected Hydrants

@ Al Hydrants I™ Generate Flushing Report (Hydrants and Blowofs)
€ Selected Junctions Nodes

 All Junction Nodes

I Report Shows All Flows As Positive Numbers





Figure 1-26 Fire Flow Calculations Set Up Screen -  Demo1-3

[image: image75.jpg]Fireflow/Hydrant Repor

Specified Minimum Pressure(psi or kPa 0
Ninimum Static Pressure(psi or kPa) 0
Sp.Min Pres@FirePump Suctn(psi or kPa] 0
Flow-1: Flowrate to maintain the specified
pressure at (hydrant) node
de-2: Node that has a lover pressure than
pecified value at Flow-1
Flov-2: Flowrate to maintain the specified
etein o e
Flov-3: Flowrate to maintain the specified
pressure at Fire Punp Suction
Hyarant  Elevation Demand  Stavic Flov-1  Flov-z  MNode-z  Flow-3 ow  NFPL
Node B Pressure apm apm gpn  Capacity  Col
HS 5150 5.0 0.1 57,3 5476 iz 7135 547.6 ORMNGE
B2 612.0 0.0 61.7 o 835.9 654.5 ORANGE
B 605 0.0 2.2 62 4804.5  3962.6  BLUE
Ho1 611.0 0.0 62.7 i 1 1644.1 a-13  2168.0  1684.1  BLUE
HE 605.0 0.0 719 3570, 4421.1  3570.6  BLUE
H-4 620. 0.0 s6 e 5476.5  4336.6  BLUE
B3 610.0 0.0 62.9 8706 as2.9 a-s  1oea.1 852.5 ORMNGE
HS 610.0 0.0 64.3 2764.3 3583.0  2764.3  BLUE
Hs 615.0 0.0 61 62.4 714.3 562.4 ORMNGE




Figure 1-27  Fire Hydrant Analysis and Report -  Demo1-3

The Set Up screen shown in Figure 1-26 will analyze all the fire hydrants in your model to calculate the fire flow available at each hydrant (one at a time) such that the pressure in the system is above 20 psi at all locations. Normally the minimum pressure occurs at the fire hydrant but it may occur at a different location. If this happens the Fire Flow Report shown above will show 2 additional columns of calculations showing the reduced fire flow and the node location where the minimum pressure occurs.

 1-6  Demo1-4 – EPS (Demo EPS.P2K)
It is a simple matter to set up an Extended Period Simulation (EPS) using the Baseline Data for the system. Care should be taken to initially clear any Change Pattern Data before setting up the EPS (select [image: image76.png]


 (KYnetic) or Setups and Defaults/Change Patterns (Classic) and click on the Clear button). To run an EPS go to the EPS Setup Screen [image: image77.png]=)



 (KYnetic) or System Data/EPS (Classic) and enter data as shown in Figure 1-28. For a municipal water distribution system such as this example a 24-hour period using a 1-hour computational period is a common selection although a shorter time period may be needed if there are numerous events during the period (tanks filling or emptying and pumps turning on and off).
KYnetic EPS menu icon: [image: image78.png]=)




[image: image79.png]Map | Map Settings [ System Data | Other Data | Setups/Defauits | Report |
‘Simulation Specifications | Other [EPS (Extended Period Simulation)]| Reports | Preferences | Skele

Extended Period Simulation (EPS)

UseEPS

Intermediate Reports 2
Total Time (hrs) [24
Computational Period (hvs) [T @ Optimal Pump Scheduling
Report Period (hrs) [T -
Default Power Cost (S/kwhr) [008
Statting Time (hrs 0:24) o

Report Time Style [WMiltary Ti

1, Control Switches




Figure 1-28  EPS Setup Screen -  Demo1-4

[image: image80.png]Name|T-1

Tank

Elevation 530

Slevationl.
My Level 755
—
Mn Level 735
Initial 750

T

1

Inflow|?
el



[image: image81.png]Elevation 525

!
1

My Level 755
Mn Level 730

Initial 749

|

Inflow|?

|




 

Tank Data: Classic 

[image: image82.png]lode Type  Tank Foxed Diamele

T

630

5

35

50

0

‘South Tank
3



[image: image83.png]730

49

0

North Tank
3




Tank Data:  KYnetic
Figure 1-29  Tank EPS Data -  Demo1-4
For an EPS the maximum (Mx) and Minimum (Mn) levels are significant items. This data shown in Figure 1-29 will cause the tanks to shutdown if either of these limits is reached. For municipal water systems the demands will vary hour by hour because of the variation in the diurnal curve as shown in Figure 1-30. This curve developed by AWWA based on field measurements provides a rational basis for varying the demands over a 24-hour period (Demand Pattern). Pipe2016 has the capability to set up, save and load Demand Patterns. An example pattern based on the AWWA curve is available (click the Load button in Demand Pattern menu and select AWWA.dmt). This Demand Pattern file is loaded as shown in Figure 1-30 and used for this example.

[image: image84.png]Peaking Fac

Figuro 2

AWWA Average Day Flow Diurnal Curve

00

80
60

40

20

00
80

60

40

20

10 15 20
Time (hours)

Figure 2

AWWA Average Day Flow Diurnal Curve

(Source:

AWWA Manual M32)





Figure 1-30  Diurnal Curve Data From AWWA -  Demo1-4

KYnetic Demand Pattern table icon:  [image: image85.png]



[image: image86.png]Pipe Type | Fittings | Sliders/Precision | Change Patterns Demand Patterns | Table Setup

Clear | Total Time [23 Time Inc

Load | Save

Pattern Name

[wAA, drt

Global Demand Factor

Time/Chang
Power Cost
Residential

Type 1
Type 2
Type 3

o [

03

1 2 3 1

02 o2

021 02

036

053

091




Figure 1-31  Demand Pattern  EPS Data -  Demo1-4

For Demo1-4 the pump is always on. For an EPS the pump status can be controlled either by inputting Change Data which can be used to turn the pump on or off at designated times or by a Control Switch which can be used to control the pump on/off status based on pressures or tank levels. This EPS example illustrates the tank action based only on demand variations.

[image: image87.png]130
128

<126

3

3

Ti24
122

120

Tank Levels (demoeps1) - no control switch

5 10
time (hours)

15

20

25




Figure 1-32  Tank Levels -  Demo1-4

[image: image88.png]Pressure

100
95
90
85
80
75
70
65
60

Pressures at J-5 and J-15 (demoeps1) - no control switch

5 10
time (hours)

15

20

25




Figure 1-33  Pressures -  Demo1-4
[image: image89.png]Flow

1200
1000
800
600
400
200

Pump Flow (demoeps1) - no control switch

5 10 15
time (hours)

20

25




Figure 1-34  Pump Flow -  Demo1-4
Figures 1-32 through 1-34 show results for this simulation. Figure 1-32 shows that the tanks are completely filled within the first 2 hours and stay full for the rest of the simulation. This causes the pump to run at a low flow and high head and produces a substantial pressure increase when the tanks fill as shown in Figures 1-33 and 1-34. Figure 1-35 shows the report on the pumping cost from the tabulated report. To obtain this report you must enter a cost/kilowatt hour as shown in Figure 1-28. 
[image: image90.png]TOTAL POVER COST(§) FOR THIS SIMULATION 36.30




Figure 1-35  Power Costs -  Demo1-4
1-6  Demo1-5 – EPS (Demo EPS Control Switch.P2K)
The results from Demo1-4 illustrate a situation which would be unacceptable for a municipal water system. The tanks cannot remain full because of water quality concerns. This example (Demo1-5) illustrates controlling the pump using the level of the water in Tank 1 (T-1). For this illustration we add a pump control switch which will turn the pump off when the water level exceeds 753 feet hydraulic grade (or 123 feet based on ground elevation). This is 2 feet below the maximum level (125 feet). The pump will then come on when the level drops below HGL = 737 feet (107 feet). The setup for this Control Switch [image: image91.png]


 + [image: image92.png]1, Contolswiches



 (KYnetic) or Other Data/Control Switches (Classic) is shown in Figure 1-36.
[image: image93.png]Control Switches | Canstraints | Calibration | Quality | Quality Calibration | Meters | Library Elements | Active Valves

Switch Units [HGL (t or m)

controlled | T on sensing below/ | low on high
is when is and when | above
element off node between | level off level

Pump-1 is on  when T-1 is below 737 and off when above 753]




Figure 1-36  Control Switch Data -  Demo1-5
The results for this EPS are shown in Figures 1-37 thru 1-39. As can be seen the pump switches off at around 2 hours and turns back on at around 14 hours. This results in less pressure fluctuations and a significantly reduced power cost (Figure 1-40)
[image: image94.png]128
124
120
S 116
©
®
T112
108
104
100

Tank Levels (demoeps2) - control switch

10
time (hours)

15

20

25




Figure 1-37  Tank Levels -  Demo1-5
[image: image95.jpg]Pump flow (demoeps?) ntrol switch
P { Ps<)

~ ®
o =]

Pressure (psi

o
=]





Figure 1-38  Pressures -  Demo1-7

[image: image96.jpg]0 15
time (hours)





Figure 1-39  Pump Flow -  Demo1-5

[image: image97.png]TOTAL POVER COST(§) FOR THIS SIMULATION 23.42




Figure 1-40  Power Costs -  Demo1-5
1-6  Demo1-6 - Water Quality Simulation (Demo Water Quality.P2K)
A water quality analysis is run using an EPS file.  This is to determine the variance in the water quality parameters over a time period (generally 24 hours).  Only one screen of additional data is required to set up the water quality analysis as shown below.  Click on the KYnetic Analysis menu as shown below or Other Data | Quality (Classic) to see the Quality input menu.
[image: image98.png]Water Quality

Water Quality Menu

Water Qualty Calbration




[image: image99.jpg]T a—
Global Bulk Reaction Rate |-125 Quality Simulation Time [144
Global Wall Reaction Rate [0.8 Time Units [Hours >

Order of Reaction - Bulk [1 = Quality Time Step [0.01 Update Tables

Order of Reaction - Wall 1 =] Quality Parameter |Chemical v |
v o

Order of Reaction - Tank |1 > | ChemicaliTank Name [chlorine
Limiting Potential [0 Attribute used for nodes *Intial Concentration®[initial Conc |
Roughness Corrrelation |0 Atribute used for nodes "Initial Age” [Initial Age v

Qualty Tolerance [0 Attribute used for pipes "Bulk Reaction Rate" [Bulk Rat

Diffusivity (sqr f/sec) [1.3E-8 > | Attribute used for pipes "Wall Reaction Rate"[Wall Rate =l

Node Source Data

Node Initial Concentration Pattern Type “




[image: image100.jpg]Reservoir Source Data

r Initial Concentration Pattern 4|
2

Pattern Data (Multlpllers)

Pattern

2




Figure 1-41  Water Quality Data

The Bulk and Wall Reaction Rates are set for all pipes using the global value shown rather than averaging values for each pipe.  A Simulation Time of 144 hours is chosen to provide ample time for the solution to reach a repeatable condition.  For this example a Chemical analysis is chosen to determine the chlorine residuals.  We could choose to calculate the age of the water (select Age) or trace the origin of the water (select Trace).  One additional useful data input is the Initial Concentration of chlorine at each node.  This can be assigned an initial value of zero.  However, a reasonable estimate of this value will provide the solution more quickly and accurately.  Since the chlorine is supplied at 2 ppm, a value of 1 ppm is used for the initial concentration and this data is assigned by using the Gbox (Group Mode) to select the entire system and the Edit Node Set to assign a value of 1.0 to the Initial Concentration.  When this is done the User Data for each node should display this data as shown below:

[image: image101.jpg]User Data

Initial Conc.
1
Initial Age

Manufacturer

Model




   [image: image102.png]Name. 1)
Elevation 610
Demand s

Demand Type 1
Title
lgnore Changes

Constraint Group,

nitial Conc 11

Initial Age.
o ar=®)





Classic - KYnetic
Figure 1-42  User Data with Initial Concentration

The Water Quality Analysis is then run by selecting [image: image103.png]


 (KYnetic) or Analyze (Classic) and Analyze | Water Quality.

Once the analysis is completed the results are reviewed.  Figure 1-43 shows the results for the minimum and maximum chlorine levels.  This is obtained by selecting Chlorine in the Results Selector – bottom right of program window and Node Results - Min and Max under Labels.

A plot of the variations in the chlorine residuals at various nodes can be shown as illustrated in Figure 1-44.

[image: image104.jpg]St
o
sl

%y

S




Figure 1-43   Min/Max Chlorine Residuals

[image: image105.jpg]Chlorine levels

chiorine





Figure 1-44   Chlorine Residuals at Selected Nodes

1-6  Demo1-7 - Optimized Calibration (Demo Calibration.P2K)
The section describes the original input approach for Optimized Calibration.  A Calibration Wizard is also available.  Figure 1-45 shows a network schematic with the test results of four fire flow tests displayed.  This fire flow test data provides the basis for performing a calibration of the distribution system. The calibration will determine the optimum value for pipe roughnesses for various groups of pipes.

[image: image106.jpg]FIRE FLOWS AND RESIDUAL PRESSURES FOR CALIBRATION (DEMOCAL)

Tank2
505GPM @36 PSI
w20

2100 GPM @39 PSI
iEL)

320 GPM @28 PSI
©-18)

‘Clear Well

350 GPM @31 PSI
©19)

Tank 1




Figure 1-45  Fire Flow Test Results
The test data include the residual flow and pressure for each of the tests.  For the calibration these four hydrants were converted to junctions as required to set up the calibration data.  For this demonstration, it is assumed that the boundary conditions (tank levels, demands, pump status, etc.) for each fire flow test were the same and that the baseline demands and the tank levels are those used for the demo model.p2k file and shown in Figure 1-46.  Thus, it is not necessary to enter change data for the four separate fire flow tests.  The only additional data required is the Calibration Data shown in Figure 1-47.

[image: image107.jpg]



Figure 1-46  Tank Levels and Baseline Demands for Calibration
KYnetic Calibration menu:  [image: image108.png]G

Calibration Wizard
Undo Cal Wiz
Calibration Wenu





[image: image109.jpg]Map | Map Settings | System Data Other Data | Setup/Defauits | Report |

Cantrol Switches | Constraints {Callration | Quality | Meters | Library Elements | Active Vahves

Attribute used for "Pipe Type"

—

Junction Pressure Data

Dernand Talerance %

Calibration Group

Fireflow Tolerance %

Junction Flow Data

Roughness Calibration
& Adjust Roughness Coeffcients

© Adjust Aging Factors

Roughness Bounds

Pipe Flow Data

CASE [JUNCTION [PRESSURE [ <] [CASE JJUNCTION _[FLow’ FIPE TYPE [UPPER_[LOWER | <
G ® I 17 20 L] o 100
] E3 420 505 1 080
R 31 19 350 B w0
CRT] ENN S8 30 E 140 100

0

System Demand Bounds

Loss Coefficient (K) Bounds

CASE [PIPE FLOW -

CASE _ [TOLERANCE %

PIPE_[UPPER |LOWER |«





Figure 1-47  Fire Flow and Calibration Data
The roughness bounds were defined for four Calibration Groups selected using various diameters as follows:

Group
Diameter

   0
  12

   1
    6

   2
    8
   3
  10
Two calibration analyses were run.  
For the first calibration a 5% tolerance was introduced for the fire flows.  This means that the fireflows can be +/- 5% of the measured residual flow and accounts for a small error in this measurement.  The calibration run produced a calibration where the optimal pressure differed from the measured pressure by only 1.4% where the difference is greater than 1.6% for the uncalibrated model. The results for the first case are shown in Figure 1-48.  
For the second case, a zero percent fireflow tolerance was used and, as expected, a larger difference of 4.8% was obtained.  These results are shown in Figure 1-49.
[image: image110.jpg]SUNMARY OF RESULTS

William coefficients: for group mumber
e b1 liamooziciedte: Fon group number
for group number
for group number

100, [140.0< >100.0

= 105. [140.0< > 80.0:
= 50. [140.0< > 90.0:
. [140.0< >100.0;

demand adjustments are made

7 R . distribucing

demands among nodes of Aiff demand types, keeping
eyt mmulliognatat: Thereimat beatleast

o ype s feature.
ction (Fire) Flow(s) for Change 1 are INCREASED by 5.00%
Finaion (Fire) Flow(s) for Change i e by 4.68%
Zunci dom{Pixe] lowle) eorichenses 3 ered NCREASID. v: (45h
ction (Fire) Flow(s) for Change 4 are INCREASED by 5.00%

TEST NODE MELSURED OPTIHAL
casE NUMBER PRESSURE PRESSURE
1 a-17 39.0 39.2
2 a-20 36.0 35.3
3 a-13 3.0 312
4 a-18 28.0 282




Figure 1-48  First Case Results (5% fire flow tolerance)
[image: image111.jpg]Hazen William coefficients: for group mmber 0 = 100. [140.0< >100.0;

Haen UsLlaom costiacionte: for growp mamber 1 - 103, [140.0< 5 o0,

Bagenlillish cossdit ienkal fof ooy ker 2o B0, L1 o< 5 o0
cients: for group muber 3

zen Williem coeffic

TEST HODE MELSURED OPTIHAL
casE NUMBER PRESSURE PRESSURE
1 a-17 39.0 40.7
2 a-20 36.0 2.6
3 a-19 3.0 311
4 a-18 28.0 30.3

= 100. [140.0< >100.0:




Figure 1-49  Second Case Results (0% fire flow tolerance)

Surge Demonstrations and Example Data Files
1  Pump Rundowns Using Pump Head/Flow Table (Pump Run Down.P2K)
1-1 2-second rundown with CV

1-2 2-second rundown without CV (flow reversal)

1-3 2-second rundown with Pressure Sensitive Demands

2 Pump Trip Using Pump File (File Pump.P2K)

2-1 Trip with CV
2-2 0.5-second rundown with CV
2-3 Trip with and without CV
2-4 10-second rundown comparing file and table
2-5 Controlled shutdown – pump and control valve
3 Pump Startups Using Pump File (Pump Startup.P2K)
3-1 2-second startup – one and two pumps
3-2 10-second startup – one and two pumps
4 Fixed and Modulating Regulating Valves (Regulator.P2K)
4-1 No modulation (Regulating Valve)
4-2 Modulation using Tool and Active Valve
5 Compressor and Bladder Closed Surge Tanks (Bladder Tank.P2K)
5-1 Compressor surge tank – 40 cubic feet initial air
5-2 Compressor surge tank – compare 30 and 40 cubic feet
5-3 Bladder tank – precharge and sizing tool – 40 cubic feet initial air
6 Valve Closures (Altitude Valve.P2K)
6-1 2-second closure
6-2 20-second closure
7 Relief Valve to Control Pressure Surge Due to Valve Closure (Pressure Relief Valve.P2K)
7-1 Add relief valve and provide data
8 Hydrant Operations (Startup and Shut Down) (Hydrant Open.P2K)
8-1 Hydrant opens in 2 and 10 seconds
8-2 Hydrant closes in 2 and 10 seconds
9 Simulated Line Break Using Rupture Disk (Rupture Disk.P2K)
9-1 Fixed demands
9-2 Pressure sensitive demands
I.   Demo1 – Municipal Water Distribution System
[image: image112.png]



                          [image: image113.png]



Figure 1   Schematic for Demo1I

The system above is used to illustrate a number of surge analyses and features of the Pipe2016 : Surge program.  The system is fed from a clearwell through a pump and a control valve.  A surge tank is shown but will be activated only for examples illustrating the use of a surge tank.  The elements noted are used to illustrate various transients and simulations such as pump, valve, and hydrant operations.  For example, the altitude valve leading to the overhead tank (Tank 1) is used to illustrate the effects of valve closure and the use of a pressure relief valve.


The screens below illustrate the data for some of the elements.  The Pipe Type Table includes wave speed data which is assigned to each pipe as the pipe type is selected.  Demands are assigned to various junctions.  A summary of the pipe and junction data is presented in Appendix A along with schematics showing pipe and nodes names.

[image: image114.png]S ETmED SystemType [suge <
Specific Gravity Additional Data

User Units | Units [GPh = Demand Calcul

Fixed Demands ~

Equation [Hazen Williams

Length Accuracy 50

Total Simulation Time [0
Wave Speed

Cavitation Head Attribute used for pipes "Wave Spee
wave speed
Default Wave Speed [4000

Time Step Increment




Figure 2   System Data
[image: image115.png]Material
d
d
d
d

Rating
150
150
150
150

Nominal Diameter Actual Diameter | Unit Cost Reference Roughness| Estimated 10yr Roughness| Wave Speed

6

8
10
12

130
130
130
130

120]

120
120
120

4200)
4150|
4100)
4050|




Figure 3   Pipe Type Table
[image: image116.png]Name[av-1
Active Valve v

Elevation 610

Cv 100%

Init Ratio
R

Valve Type
Butterlly =l

|




[image: image117.png]


[image: image118.png]Name[av2
Active Valve v

Elevation 530

Cv 100%

Init Ratio




[image: image119.png]



Active Valve data:  Classic and KYnetic

[image: image120.png]Name[Ryvel

Regulator <

Elevation 530

——

Setting 40
iy

Regulator Type
PSv ~

|



[image: image121.png]



Regulator Data:  Classic and KYnetic
Figure 4    Valve and Regulator Data
 1  Pump Rundowns Using Pump Head/Flow Table (Pump Run Down.P2K)
1-1  2-second rundown with CV
1-2  2-second rundown without CV (flow reversal)
1-3  2-second rundown with Pressure Sensitive Demands
For Case 1, a pump table is used to describe the pump and the data is presented in Figure 1-1.  Case 1-1 is carried out using a 2-second pump rundown set up using change data shown in Figure 1-2.  For Case 1-2 the check valve is removed and for Case 1-3 the analysis is carried out using Pressure Sensitive Demands.  Results are shown in Figures 1-3 to 1-5.

[image: image122.png]Name|Pump-1

Pump E

D
Head| Flow Eff%

Elevation|510 20 0 o
et |l e 77
Sp Ratio|! 1601200 70,

—_—

~Pump Type
& Table  File
© Const” Rated




[image: image123.png]Device Data
v Time 0.1

CV Res[0.05

Byps Res!

W Check Valve
I~ INSRREHER TV
I~ Bypass Line



[image: image124.png]More Device Data

Pump Res[0.05




Pump Data - Classic

[image: image125.png]Pump - Table




[image: image126.png]Pump Curves

1
Pressure Head

Head Flow Effiency





Pump Data - KYnetic
Figure 1-1  Pump Table Data (With CV)

[image: image127.png]Node Changes

cut] copy| Paste] ctea

Time/.
Case

Value




[image: image128.png]Changes for Pump-1

[rime

[change

[Valie

Speed ratio
speed ratio
speed ratio

1

1

o




Pump Rundown Data:  Classic - KYnetic

[image: image129.png]Device Data
v Time 0.1

[

CV Res|

Byps Res|

I~ Check Valve
I~ NonReopen CV.
I~ Bypass Line



[image: image130.png]Pump - Table

Bypass Line




No Check Valve in Pump:  Classic – KYnetic

[image: image131.png]Demand Calcul.

Fixed Demands ~

Fixed Demands





Demand Modeling

Figure 1-2  Additional Data Screens
[image: image132.png]120

100

@
=]

Pressure

Pressure at J-11 - 2 second rundown (with cv)

20

30
time (sec)

40

50

60




[image: image133.png]Pressure

120

100

80

60

40
20

=)

Pressure at J-11 - 2 second rundown (with cv) (180 sec)

20

40 60 80 100 120 140 160
time (sec)

180




Figure 1-3   Results for Case 1-1
[image: image134.png]Pressure

120

100

80

60

40

20

Pressure at J-11 - 2 second rundown (with & w/o cv)

10

20 30 40 50
time (sec)

60



[image: image135.png]Flow

1500
1000
500

-500

-1000

Flow through pump - 2 second rundown (with & w/o cv)

-1500+
0

10

20 30 40 50
time (sec)

60




Figure 1-4   Results for Case 1-2
[image: image136.png]Pressure

120

100

80

60

40

20

Pressure at J-11 - 2 second rundown (with cv)

10

20 30 40 50
time (sec)

60




Figure 1-5 Results for 2-Second Pump Rundown with Pressure Sensitive Demands
2  Pump Trip Using Pump File (File Pump.P2K)
2-1  Trip with CV
2-2  0.5-second rundown with CV
2-3  Trip with and without CV
2-4  10-second rundown comparing file and table
2-5  Controlled shutdown – pump and control valve together
                             [image: image137.png]Name[Pump-1
P

Elevation 610

—
Sp Ratio!
—

Effcny% .77

pldll el SO

Purp Type
 Table & File
 Canst(™ Rated




[image: image138.png]Device
CV Time|

CV Res:
File (1-8)
Rated Hd
Rated Fl]

Rated Spd

Inertia

Data
o1

005

165
1140

1200
ez

W Check Valve

I NonRea
I~ Bypass

pen OV
Line



[image: image139.png]Node Changes

] | i

Time/.
Case

o sh
1t T

Value





File Pump Data and Change Data – Classic

[image: image140.png]Elevation

Title

Parallel

Check Valve

plon-Reopening Che

Bypass Line

CV Time.

CV Resistance.

Eficiency %

Speed Ratio

Grade

File# (120)

Rated Head

165

Rated Flow

1140

Rated Speed

1200

Inertia

pump Resistance.

Bypass Resistance|

Direction

on/off




[image: image141.png]Changes for Pump-1

[rime [change Vale
v Speed ratio 1
1 trp e





File Pump Data and Change Data - KYnetic
Figure 2-1  Pump File Data and Pump Trip Data


Figure 2-1 shows the data screens used to describe the pump using a pump file.  This approach is recommended for modeling a pump file because the rundown time is computed based on pump characteristics.  In most cases users will only have head/flow data for normal operations.  When using one of the Pipe2016 : Surge pump files for modeling a pump trip, it is recommended that the operating point for the initial steady state operations be used for the Rated Head and Rated Flow (1140 gpm @ 165 feet).  This will assure that the starting conditions will match the one obtained using the head/flow curve.  Pipe2016 : Surge tools are available for selecting the appropriate pump file and defining the inertia.  The use of these tools is illustrated in Figure 2-2.  It is assumed that the pump speed and efficiency are available data.

The Change Data setup for a pump trip initiated 1 second into the simulation is shown in Figure 2-1.  A 60-second pressure history for node J-11 is shown in Figure 2-3 and the pump speed history is shown in Figure 2-4.  This plot shows that the pump rundown occurs very rapidly over approximately 0.5 seconds.  A principal benefit of simulating a pump trip is that the rundown time is calculated.  Figure 2-5 compares the pressure history at J-11 for a pump trip and a 0.5-second pump rundown.  The nearly identical results are due to two factors:

1. the rundown time of 0.5 seconds is very close to the predicted one,

2. the rapidly closing check valve presents abnormal pump operation.

   [image: image142.png]Engish
Fump Speed N ()
Flow Rate @ (gpr)
Fump Head h (1)
Effciencyn (010 1)

Fump Fowe (HF)

Specific Speed (CopyRight: KYPIPELLC 2013

1200
[ad
—
077
[eies |

INERTIA (1bit"2)

Faily Dld Pumps|
Smal, ght wt Punps|
Motor netia
Comb Ineti (od pups)
Comb Ineti (smallpurps)

Caloulated Ineftia s WR"2
Specitic Speed.
Suggested Pump File

T

FORMULAE Fump Fower

7 Qersf,
5501

asssa
HP }

L =0.6674x| 2o
fid {(N/IOOO)

Inesta for smal, ght wt punps

I
{1000}

HP

Inesta for iy ol pumps.

Iy =0 6244{

Mator Inetia
20.33 e
HP
Iy =0.0648x|
1276 (y1000)
o | ecfesmesd
Spepeed = 22
124 HA
EEg Purnp Fl | SpeSpeedEng]_SpeSpeed I
. T 1270 =
(NOT 6D"2) 2 7600 w7
T 3 13500 1
860.08 4 3725 72
i 5 ) &
6 ) 101
Close 7 o2 3
8 8764 169




 
Figure 2-2  Tools for Pump File Data

[image: image143.png]160
140

Pressure

N B ® ® O N
© © o o S o

o
S o

Pressure at J-11 - Pump trip (with cv)

=)

10

20

30 40
time (sec)

50

60




Figure 2-3   Results for Case 2-1

[image: image144.png]Node Graph  Default Scale ¥ Titles

14
Small| Print (5] Y min [20 Topfeed - T S22 s
arg| Range| Setup| ¥ M2 [120 Left _Capture to BMP |
I~ Previous Resut " 9 [20 Bottorrtime (sec)  Copy to Clipboard|
Pump Speed (rpm) - Pump trip (with cv)
1400
1200
1000
3 800
o
a
@ 600
400
200
ol
-10 0 10 20 30 20

time (sec)




Figure 2-4   Results for Case 2-1

[image: image145.png]0.5 second Pump rundown - Pump trip (with cv)

time (sec)




Figure 2-5   Results for Case 2-1 and 2-2
[image: image146.png]Pump Flow (gpm) - Pump trip (with and w/o cv)

20 30 40 50
time (sec)

60




Figure 2-6   Results for Case 2-3

The Change Data setups for two additional simulations (Cases 2-4 and 2-5) are shown in Figure 2-7.  The results for Case 2-4 are shown in Figure 2-8 and show the pressure history for J-11 for a 10-second rundown using both a pump head flow table and a pump file setup as described previously.  The results illustrate 2 points:

1 the pump table and pump file give very similar results if abnormal pump operation is avoided,

2 pump shutdown can be controlled to limit the range of the pressure surges.

Case 2-5 illustrates a shutdown which combines the closing of a control valve and ramping down the pump (Figure 2-9).  Pipe2016 : Surge can be used to determine effective techniques for turning off pumps.
[image: image147.png]Node Changes

o] e

Time/.
Case

Value




  [image: image148.png]Changes for Pump-1

[rime

[Change

Valie

11

Speedratio
speed ratio
speed ratio

1

1

o




10-Second Pump Rund own: Classic - KYnetic

[image: image149.png]Node Changes

s o]

Time/.
Case

Value




[image: image150.png]Changes for AV-2

[rime

Valie

§§§

1

o




25-Second Valve Closure

[image: image151.png]Node Changes

cut] copy| Paste] e

Time/.
Case

Value




[image: image152.png]Changes for Pump-1

|ime change [Vale
o speed ratio T

15 speed ratio 1

> Tspeedrat

o




 10-Second Pump Rundown
Figure 2-7   Data Screens for Cases 2-4 and 2-5
[image: image153.png]90

80

70
e
=60
2 50
a

40

30

20

10 second Pump rundown - Pump table & Pump file (with cv)

20

30 40
time (sec)

50

60




Figure 2-8   Results for J-11, Case 2-4
[image: image154.png]10 second Pump rundown - Control VValve Closure (25 sec.)

10 20 30 40 50 60
time (sec)




Figure 2-9   Results for J-11, Case 2-5 compared with Case 2-4
3   Pump Startups Using Pump File (Pump Startup.P2K)
3-1  2-second startup – one and two pumps
3-2  10-second startup – one and two pumps
[image: image155.png]Node Changes

] ]

Time/.
Case

Value




[image: image156.png]Changes for Pump-1

[rime

[Change

Valie

Speed ratio
speed ratio
speed ratio

o

o

1




2-Second Startup

[image: image157.png]Node Changes

Time/.
Case

Value




[image: image158.png]Changes for Pump-1

[rime

[Change

Valie

11

Speedratio
speed ratio
speed ratio

o

o

7




10-Second Startup

[image: image159.png]0t |Less <y et User

Name[Fump-1
[Fums -]
Elevation 610

—

Sp Ratio [

AL

Effcny% /77

———

Purp Type
 Table & File
 Canst(™ Rated

.. &




[image: image160.png]Name[Pump-1
Pump <]
Elevation 610
ool

Sp Ratio [

AL

Purp Type
@ Table C File
€ Canst™ Rated

P o




[image: image161.png]Pump - Table
Pump-1
610

2 Parallel
7




Single Pump                                2 Parallel Pumps

Figure 3-1  Data Screens for Cases 3-1 and 3-2

[image: image162.png]Pressure

2-second Pump Startup - 1 and 2 Pumps - Pump Discharge Pressure

0 40
time (sec)




Figure 3-2   Results for Case 3-1

Several pump startup scenarios are set up as shown in Figure 3-1.  Note that a pump which is initially off should be designated as such by clicking on the off button (top of the Node Information window in Classic or On/Off row in KYnetic).  This will result in a red X imposed on the pump symbol on the map.  Either pump description (pump table or file) can be used.  Also the Pipe2016 : Surge feature for handling multiple pumps is illustrated by running two simulations:

a) startup a single pump,

b) startup 2 parallel pumps.

Results are shown in Figures 3-2 and 3-3 for a 2-second and a 10-second (soft start) startup.   A point of interest is that the pressure surge is not greatly affected by this difference in start time.  This is because the pump must reach around 85% of full speed before the check valve can open and create a pressure spike.  All the transient action occurs in the short period after the cv opens.

[image: image163.png]Pressure

10-second Pump Startup - 1 and 2 Pumps - Pump Discharge Pressure

0 40
time (sec)




[image: image164.jpg]10-second Pump Startup - 1 and 2 Pumps - Pump Discharge Flow

0 40
time (sec)




Figure 3-3   Results for Case 3-2
4  Fixed and Modulating Regulating Valves (Regulator.P2K)
(see also Training Exercise #1)
4-1  No modulation (Regulating Valve)
4-2  Modulation using Tool and Active Valve
[image: image165.png]REGULATING VALVE REPORT

VILVE  VALVE  VALVE  VALVE UPSTREAN DOWNSTRERH THROUGH
(psi or gpm) (psi) (psi)  (gpm)

RV-1  PSV 40.00 ACTIVATED  40.00 4.08 425.56




[image: image166.png]REGULATING VALVE REPORT

VILVE  VALVE  VALVE  VALVE UPSTREAN DOWNSTRERH THROUGH
(psi or gpm) (psi) (psi)  (gpm)

RV-1  PSV 40.00 ACTIVATED  40.00 7.14 s78.09




Figure 4-1   Initial and Final Steady State Results for Regulator

Pipe2016 : Surge treats modeled regulating valves (PRVs, PSVs, and FCVs) as constant resistance valves and computes the resistance based on the initial conditions.  This approach is based on the concept that for fast transient events, the regulating valves may be unable to respond.  Figure 4-1 shows the Regulating Valve Report for two steady state scenarios with a PSV set at 40 psi.  For the upper one no pumps are operating and for the lower one two pumps in parallel are operating.
[image: image167.png]Pipe2000 - Modulating Valve Settings (CopyRight: KYPIPE LLC 2004)

Unis
@ Engish 51 | C Head & Pressue Resistance - Headlass / {Flow"2},
where Headlass s in feet or meters
Sp.Graviy=[1  Flowsts [on <] | and Flowis in cubicfest per second
or cubic meters per second
€ Wide Dpen Resitance

1000 @ Flow Coefficent

Flow Coefficient = Flow (in gpm or
m°3/hr) thet develops a pressure
drop of 1 psi or 1 bar across the valve
Iniial teady Stete Condiions
Upstream Pressure [g5 — psi
Moduation Settngs

Downstieam Pressure [435 psi
Wide-open Resstance 0.4649
Flowate [1555
Iniial Ratio [§ 570
Finsl Steady State Condiions

FinalRlio [g700
Upstieam Pressure [ psi

Downstieam Pressure [7.14 psi
Ext
Flowate 57508




Figure 4-2  Tool for Modulating Valve Calculations
[image: image168.png]Name[av-3
[active vave ]

Elevation 530

Cv 100%1000

Init Ratio|0.07
TRLCET) e

Valve Type
[corao -]




 [image: image169.png]Active Valve.
Av3
630




 
Active Valve Input Data

[image: image170.png]Node Changes

Time/.
Case

cut

Value



[image: image171.png]Changes for AV1

[rime

Valie

007

007

01




Active Valve Change Data
Figure 4-3 Active Valve Setup for Modulating Valve
[image: image172.png]Pressure
I IS o
=) S =)

N
=]

Pressure at Regulator Inlet - (with & w/o modulation)

20

40 60 80 100 120 140 160
time (sec)

180




Figure 4-4    Results for Case 4-1
Case 4-1 illustrates the transient response to a two-pump startup using the Pipe2016 : Surge default approach.  The resistance is based on the initial pressure drop (35.95 psi) at the initial flow (425.56 gpm) as shown in Figure 4-1.  Case 4-2 illustrates the same transient using a Modulating Active Valve.  Figure 4-2 illustrates the use of the Pipe2016 : Surge Modulating Valve Settings tool.  The data shown on the screen was obtained from the steady state results depicted in Figure 4-1.  The settings for the Modulating Active Valve are shown in Figure 4-3.

Figures 4-4 and 4-5 show results for the two methods of handling regulating valves.  As shown, the responses are significantly different and it is important for a user to choose the most appropriate method for their application.

[image: image173.png]600 Flow Thru Regulator - 2 pumps start (with & w/o modulation)

575
550
525
é 500
475
450
425
400

0 20 40 60 80 100 120 140 160 180
P-20




[image: image174.png]Pressure

100 Pressure at J-11 - (with & w/o modulation)

90
80
70
60
50
40
30
20

0 20 40 60 80 100 120 140 160 180
time (sec)




Figure 4-5    Results for Case 4-2
5  Compressor and Bladder Closed Surge Tanks (Bladder Tank.P2K)

5-1  Compressor surge tank – 40 cubic feet initial air
5-2  Compressor surge tank – compare 30 and 40 cubic feet
5-3  Bladder tank – precharge and sizing tool – 40 cubic feet initial air
A compressor surge tank is positioned downstream from the pump station as shown in Figure 1.  This element has been disabled for the previous cases as shown in Figure 5-2.  Pipe2016 : Surge provides an on/off button for this purpose and displays a red X when off.  For Case 5-1 the surge tank is activated as a shown in Figure 5-3.  For this example the tank is connected to the 12-inch line with a 6-inch pipe.  The resistance of the connection is computed using the Resistance Calculation tool as shown in Figure 5-1.  For a compressor type surge tank, the most significant parameter affecting the response is the initial volume of air which is maintained under the initial steady state pressure.  The Tank Volume has no affect on the calculations but needs to be somewhat greater (~20%) than the maximum air volume which occurs during transient operations.  The Exp(ansion) constant will be between 1.0 (isothermal) and 1.4 (adiabatic) and a value of 1.2 is recommended if the expansion process is not known.

[image: image175.png]= Pipe2000 - Resistance Calculation Tool (... [X

Unit[Engish  ~]

Caloulate Resistance From [Connacton to Tark.

No.of ebows [
Fipe Diameler |5 in

Lengthof Ppels

Addiional ks[5

Compute Resistarce.

Resitnce= [30





Tank Resistance Tool
[image: image176.png]Narne[SDO-1
Closed Srg Tnk =]

Elevation 610

e —

inflow R|1-3
miowRl—__

Outflow R|1-3
towRl -




[image: image177.png]Device Data
Tank Vol [120

In Gas Vol [10

Exp Con[12

I~ Hybrid Tank



            [image: image178.png]Eode Typ:e "Verl Closed Surge

Name 'SDO1
Elevation 610
Title

On/Oft Ev4

nflow Resistance 13
Outfow Resistance 3.
Tank Volume 120
niial Gas Volume 40

Expansion Constani 1 2.

Diameter l
Iniial Level 4
Hybrid

Elevation Difference



                     Compressor Tank Data
Figure 5-1  Tool and Data Screens for Case 5
[image: image179.png]


[image: image180.png]ot [Less eq] er User
Narne[SDO-1
Closed Sy Tk ~|

B0

Elevation
—

Inflow RI13
——

Outflow R|1 3
i )




 [image: image181.png]



Figure 5-2  Surge Tank Location turned Off
[image: image182.png]


  [image: image183.png]el More. > | Data] Ching
T Less, ey ron User
Nare[SDO-1

Closed Srg Tk ~|

610

Elevation
—

Inflow RI13
——

Outiow R[1-3
ol —__




 [image: image184.png]



Figure 5-3  Surge Tank Location turned On
[image: image185.png]Pressure

Pressure at J-11 with & w/o compressor surge tank

20

40 60 80 100
time (sec)

120




Figure 5-4    Results for Case 5-1

Figure 5-4 shows the pressure history at J-11 with and without the compressor tank following a pump trip.  This shows that the surge tank provides very good protection.  
[image: image186.png]Pressure

@
S

~
o

@
=]

o
=)

I
=)

w
=]

N
=]

Pressure at J-11 with compressor surge tank (40 & 30 initial air vol ( cf))

20 40 60 80 100 120
time (sec)




Figure 5-5    Results for Case 5-2

Figure 5-5 shows also the response with a smaller initial air volume (30 ft^3).  This shows that the smaller air volume results in larger pressure transients and a higher perturbation frequency.  
[image: image187.png]Volume of air with compressor surge tank

20

40 60 80 100
time (sec)

120




Figure 5-6    Results for Case 5-2 (to size Bladder Tank)

Figure 5-6 shows the variation in the volume of air during the transient.  This information is required to size the surge tank (to contain the air with a safety factor) and also to calculate parameters for a Bladder Surge Tank which will provide the same protection.  Because of the requirement to define the precharge pressure for a bladder tank it is recommended that the surge analysis be initially carried out using a compressor tank and varying the initial volume of air until an acceptable result is obtained.  Then the Bladder Precharge tool can be used as shown in Figure 5-7 to calculate the required tank volume and precharge pressure (head).  Data for the Bladder Tank can then be entered as shown in Figure 5-8.
[image: image188.png]Pipe2000 - Bladder Tank (CopyRight:

Unis
& Engish ca
Volume:
 Galons & Cubio Feet
Pressue
© pal  Fest

Flatm) = 3382t or 147 psi
Flatm) = 10.34m or 101 435KPa

KYPIPE LLC 2004)

Masinum AitVolume [5
Iniicl i Pressure [{555
Iniial it Volume [55

Frecheige Pressure

Bladder Volume

Close.




Figure 5-7  Bladder Precharge Tool  Case 5-3

[image: image189.png]Name[SDO-2
Bladder Tank  ~|

Elevation 510
—
Inflow RI13

il )

Outow RI1 3
i ) L




[image: image190.png]Device Data

Tank Vol [72
Exp Con[12
Preset Hd[73

I Use Pressure



 [image: image191.png]Vert Bladder Tank





Figure 5-8  Bladder Tank Data Screen  Case 5-3
[image: image192.png]Pressure

@
S

~
o

@
=]

o
=)

I
=)

w
=]

N
=]

Pressure at J-11 with compressor and bladder surge tank (72 cf)

20 40 60 80 100 120
time (sec)




Figure 5-9    Results for Case 5-1 and Case 5-3
Figure 5-9 shows the results for a compressor tank with an initial air volume of 40 ft3 (case 5-1) and an equivalent bladder tank (case 5-3).  As shown, the solutions are virtually identical.
6  Valve Closures (Altitude Valve.P2K)
6-1  2-second closure
6-2  20-second closure
Cases 6-1 and 6-2 illustrate transients due to a valve closure.  A 2- and 20-second closure of the altitude valve for Tank 1 are simulated.  Figure 6-1 shows the data screen for the valve and the Change Data to produce the valve closure.  The valve is a gate valve.

Figure 6-2 shows the results for both the 2-second (case 6-1) and the 20-second (case 6-2) closures and, as expected, the more rapid closure produces the larger pressure surge.  For this case the pressure surge exceeds 200 psi which could be excessive.

[image: image193.png]Name[av2
Active Valve v

Elevation 530

Cv 100%

Init Ratio




 [image: image194.png]


 
Gate Valve Data

[image: image195.png]Node Changes

Timel o

Case




 [image: image196.png]Changes for AV-2

[rime

Valie

§§§




2-Second Valve Closure

 [image: image197.png]Node Changes

] |

Time/.
Case

Value




 [image: image198.png]Changes for AV-2

[rime

Valie

§§§




20-Second Valve Closure
Figure 6-1   Data Screens for Altitude Valve and 2- and 20-second Closures
[image: image199.png]Pressure at Altitude Valve (2 and 20 second closures)

20 30 40 50
time (sec)

60




Figure 6-2    Results for Case 6-1 and Case 6-2
7  Relief Valve to Control Pressure Surge Due to Valve Closure (Pressure Relief Valve.P2K)
7-1  Add relief valve and provide data
                         [image: image200.png]



Figure 7-1  Location of Altitude Valve Relief Valve

A 6-inch relief valve was inserted a short distance downstream from the Tank 1 altitude valve as shown above (Figure 7-1).  The wide-open resistance of the valve was computed using the Resistance Tool and considering the resistance for a 6-inch orifice.  This is illustrated in Figure 7-2 along with the input data for the relief valve.  The opening pressure, opening time, closing pressure and closing time were chosen based on the expected steady conditions with the altitude valve open and closed.  The External Head is input as zero indicating that the relief valve vents to the atmosphere.

Figure 7-3 shows pressure histories at the altitude valve and at J-11 with and without the Relief Valve in service.

[image: image201.png]pe2000 - Resistance Calculation Tool

Uit [Engish

Caloulate Resistance Fiom [Grfcs Data
Cosif.of Dischaige [752

Oifice Diameter[§—— in

Compute Resistarce.

Resistance = [1.0432814904





Resistance Calculation Tool

[image: image202.png]Name[ERIGET
Prs RIf Vv hd

Elevation 530
—
Inflow 105

il )

Outfiow R|1.05
il ) L




[image: image203.png]Device Data
Open Pr[100

Open Tm
Cls Pr|
Cls Tm
Extnl Head

Sensing N
I™ Use Head



 [image: image204.png]Node Type ~ Pressure Relief

IName SDO-2
Elevation 630
itle

nfow Resistance (1,05
Joutfow Resistance1 05
IOpen Pressure (100
Open Time 5
(Close Pressure 50
Close Time 5
Extemal Head 0
ISensing Node




Pressure Relief Valve Data
Figure 7-2  Resistance Tool for 6-inch Relief Valve Resistance and Data Screens
[image: image205.png]Pressure at Altitude Valve (with & w/o 6 inch relief valve)

time (sec)




[image: image206.png]Pressure

120

100

80

60

40

20

Pressure at J-11 (with & w/o 6 inch relief valve)

20

30 40
time (sec)

50

60




Figure 7-3    Results for Case 7-1
8  Hydrant Operations (Startup and Shut Down) (Hydrant Open.P2K)
8-1  Hydrant opens in 2- and 10-seconds
8-2  Hydrant closes in 2- and 10-seconds
[image: image207.png]



Figure 8-1  Location for Fire Hydrant

Figure 8-1 shows the location of a fire hydrant which is changed to a junction to analyze hydrant startup and shutdown scenarios.  A steady state analysis is conducted to show that a fire flow in excess of 1850 gpm could be pumped from that location and still maintain a residual pressure of 20 psi throughout the system.  However, the steady state analysis does not address the transient low pressures which can develop during startup and high pressures due to shutdown.  In order to illustrate this, 2-second and 10-second startup and shutdown scenarios were modeled for a fire flow of 1800 gpm.  The data screens for the startup are shown in Figure 8-2 and the results for the pressure at J-11 are shown in Figure 8-3.  The corresponding information is shown in Figures 8-4 and 8-5 for the shutdown.

This exercise effectively illustrates that while a system may be able to deliver a specified fire flow and maintain the required residual pressure, care must be taken during the startup and shutdown of the hydrant to avoid excessive high and low pressures.
[image: image208.png]Namej.-15

[Junction

Elevation|511

Dermand
(I

Drm Type;

‘




 [image: image209.png]Hunction





Junction Data

[image: image210.png]Node Changes

] o e

Time/.
o Value

40
40
d 1800




 [image: image211.png]Changes for J-13

[Fme [change. [Value
3 demand o
2 demand o
+ demand 1200





2-Second Hydrant Open

[image: image212.png]Node Changes

cut] copy| Paste] ctea

Time/.
Case

Value

0 4o
2 4o
12 d 1800




 [image: image213.png]Changes for J-13

e [change. [Value
g demand o
2 demand o
2 demand 1200





10-Second Hydrant Open
Figure 8-2  2-second and 10-second Hydrant Startup
[image: image214.png]Pressure

140
120
100

Pressure at J-11 - Hydrant opening (2 & 10 seconds)

20

40 60 80 100 120
time (sec)




Figure 8-3    Results for Case 8-1
[image: image215.png]Namej)-13

[Junction

Elevation|511

e —

Dernand| 1800

D Typefi ~




 [image: image216.png][ode Type Juncton Smgi Der

IName 13
Elevation 611
IDemand 1800




Junction Data with Initial Demand

[image: image217.png]Node Changes

o

Time/.
o Value
d/1800
d 1800

40




 [image: image218.png]Changes for J-13

Time. [change Valie
0 ‘demand 1800
2 demand 1800

o




2-Second Hydrant Closure

[image: image219.jpg]Nod
Time/
Case VAU

d 1800




 [image: image220.png]Changes for J-13

[rime

[Change Valie
o ‘demand 1800
2 demand 1800

12

o




10-Second Hydrant Closure
Figure 8-4  2-second and 10-second Hydrant Shutdown
[image: image221.png]Pressure

200

o
=)

=)
=]

o
=)

Pressure at J-11 - Hydrant closing (2 & 10 seconds)

20

40 60 80 100
time (sec)

120




Figure 8-5    Results for Case 8-2
9  Simulated Line Break Using Rupture Disk (Rupture Disk.P2K)
9-1  Fixed demands
9-2  Pressure sensitive demands
[image: image222.png]



Figure 9-1  Location of Rupture Disk to simulate Line Break

Pipe2016 : Surge features a very useful surge control which can be used to simulate a line break.  A rupture disk with a pressure setting below the initial pressure at the rupture disk will activate at the start of a transient simulation.  This will simulate a system operating at steady state which suddenly experiences a catastrophic break which results in flow exiting the system through the opening.  The only data required is the resistance of the opening through which the water exits the system.


Figure 9-1 shows the location of a rupture disk inserted in an 8-inch main to simulate the line break.  The Resistance tool is used to calculate the resistance through an 8-inch circular opening exiting to atmosphere.  An activating (opening) pressure of 20 psi which is well below steady state pressure is input as shown in Figure 9-2.


Results for the pressure at J-11 are shown in Figure 9-3 using the Fixed Demand option ([image: image223.png]


 or System Data | Simulation Specs).  Since it is highly unlikely that the initial demands can be maintained, a second scenario is carried out using Pressure Sensitive Demands (Figure 9-4).  Although less severe, this transient produces cavitation and low pressure throughout the distribution system.
[image: image224.png]= Pipe2000 - Resistance Calculation Tool (CopyRi

Uit [Engish

Caloulate Resistance Fiom [Grfcs Data
Cosif.of Dischaige [752

Oifice Diameter[g —— in

Compute Resistarce.

Resstrce= [033





Resistance Calculator Tool
[image: image225.png]Name[SDO-2
Rupture Disk =]

Elevation 590
—
Inflow RI0-53

il )

Outfow R[5
towR|FH




[image: image226.png]Device Data

Open Pri20]

I Use Head



 [image: image227.png]Infiow Resistance 0.33

Jouttow Resistance0 33

lOpen Pressure 20




Rupture Disk Data
Figure 9-2  Resistance Tool – 8-inch Line Break and Rupture Disk Data Screens
[image: image228.png]Pressure
2 2 o
S 38 o

)
o

Pressure at J-11 - 8 inch main break (fixed demands)

20 30 40 50
time (sec)

60




Figure 9-3    Results for Case 9-1
[image: image229.png]Pressure

@
=]

@
=]

I
=)

N
o

=)

o
S

Pressure at J-11 - 8 inch main break (pressure sensitive demands)

10 20 30 40 50 60
time (sec)




Figure 9-4    Results for Case 9-2
10  Simulated Pump Trip Using Inflow Node (Negative Demand.p2k) 
      An additional alterative for modeling a pump shutdown (including pump trip) is to model the pump as a junction Node with a negative demand which inputs the operating pump flow. This will result in a head at the node equal to the pump discharge head at the operating flow condition. Figure 10-1 shows the setup for modeling the same pump used for Cases 1 and 2 (1141 gpm @ 165 feet).  Data screens are shown in Figure 10-2 for the Pump Node and a 3 second rampdown of the flow to simulate a pump trip. The results are shown in Figure 10-3.

                             [image: image230.png]


 

Figure 10-1    Modeling an Inflow (Pump) Node
[image: image231.png]


    [image: image232.png]Junction Single

13
610
a1
7




Junction Data with Inflow

[image: image233.png]


  [image: image234.png]Changes for J13

[rime

[Change

Valie

demand

demand

T




Rampdown of Junction Demand

Figure 10-2   Data Screens for Pump Junction Node  3-Second Rampdown
[image: image235.png]Pressure (psi)

140
120
100

r O @
S © o

Pressure at J-11 - 3 second rundown of 1141 gpm

20

40 60 80 100
time (sec)

120




Figure 10-3    Results for Case 10
 Figure 10-4  shows the results previously presented for simulating a pump trip by:
1) ramping down the pump speed from full (1) to zero in 2 seconds
2) using a pump file based on operating conditions and calling for a pump trip
All three approaches produce similar results. One advantage of using a Pump Junction Node is that details about the pump station are not required (check valve characteristics, etc). This approach also eliminates instabilities (excessive pressure spiking) due to check valve action and cavitation.  It may also be argued that this is a relatively conservative approach because all flow provided by the pump is removed subjecting the pipeline to a maximum downsurge. However, this approach will not account for effects such as flow reversal through the pump due to check valve closing delays. 
[image: image236.png]120

100

@
=]

Pressure

Pressure at J-11 - 2 second rundown (with cv)

20

30
time (sec)

40

50

60




[image: image237.png]160
140

Pressure

N B ® ® O N
© © o o S o

o
S o

Pressure at J-11 - Pump trip (with cv)

=)

10

20

30 40
time (sec)

50

60




Figure 10-4    Comparing Results for Pump Trip Modeling  (Cases  1 and 2) 
Appendix 1-A   Demo1 – Municipal Water Distribution System
[image: image238.png]



[image: image239.png]



Figure I-1   Pipe Names

[image: image240.png]



Figure I-2   Node Names

Demo1 -  Pipe and Node Data
   P I P E              NODE NAMES     LENGTH  DIAMETER  ROUGHNESS    MINOR 
   N A M E             #1        #2                    (ft)               (in)                COEFF.     LOSS COEFF.
 -------------------------------------------------------------------------------
       P-1            J-2        J-10                   2844.00          6.00                130.0000      0.00
      P-10           J-10      J-14                  1649.00           8.00                140.0000      0.00
      P-11           J-10      J-11                  2801.00           6.00                130.0000      0.00
      P-12           J-12      J-16                   1464.00          8.00                140.0000      0.00
      P-13           J-12      AV-2                 2131.00          8.00                140.0000      3.40
      P-14           J-15       J-1                   2550.00           8.00                140.0000      0.00
      P-15           J-16       J-3                   1753.00         10.00                120.0000      0.00
      P-16            J-4        J-7                  1532.00           8.00                 140.0000      0.00
      P-17            J-4        J-14                2938.00           8.00                 140.0000      0.00
      P-18           J-14       J-8                  1942.00           8.00                 140.0000      0.00
      P-19            J-7        J-10                3447.00           8.00                 140.0000      0.00
       P-2            J-3        J-15                 2059.00          10.00                120.0000      0.00
      P-20            J-7       RV-1                 657.00            6.00                130.0000      0.00
      P-21      Pump-1     R-1                   250.00          12.00                 120.0000      7.50
      P-22      @~RV-1       R-2                613.00            6.00                 130.0000      0.00
      P-23         AV-1  @~Pump-1             50.00          12.00                 120.0000      0.00
      P-24         SDO-1    @~AV-1             50.00          12.00                 120.0000      0.00
      P-25         @~AV-2       T-1              355.00            8.00                 140.0000      0.00
       P-3            J-3     SDO-1                  100.00          12.00                 120.0000      6.40
       P-4            J-1       T-2                    2337.00            8.                     140.0000      1.90
       P-5            J-1       J-6                    3296.00             8.00                140.0000      0.00
       P-6            J-6       J-5                    1983.00             6.00                 130.0000      0.00
       P-7            J-6       J-4                      686.00             8.00                 140.0000      0.00
       P-8            J-8      J-12                    2633.00            8.00                 140.0000      0.00
       P-9            J-8       J-9                     3138.00            6.00                 130.0000      0.00
       NODE      NODE      EXTERNAL  JUNCTION    EXTERNAL  
       NAME      TITLE      DEMAND     ELEVATION    GRADE    
                                               (gpm)                    (ft)                  (ft)    
    --------------------------------------------------------------
       AV-1                                   0.00       610.00
       AV-2                                   0.00       630.00
        J-1                                      9.00       607.00
       J-10                                   15.00       611.00
       J-11                                   45.00       610.00
       J-12                                    0.00       610.00
       J-14                                    0.00       610.00
       J-15                                    0.00       605.00
       J-16                                    0.00       605.00
        J-2                                   75.00       617.00
        J-3                                     0.00       605.00
        J-4                                     0.00       602.00
        J-5                                   45.00       613.00
        J-6                                   21.00       611.00
        J-7                                     0.00       613.00
        J-8                                   18.00       611.00
        J-9                                   30.00       615.00
     Pump-1                               0.00        610.00
        R-1                                      ----       605.00         610.00
        R-2                                      ----       630.00         630.00
       RV-1                                    ----       630.00         722.31
      SDO-1                                   .00       610.00
        T-1    South Tank              ----       630.00         750.00
        T-2    North Tank              ----       625.00         749.00
Section 2 - Class Exercises


Class Exercise 1 - Quick Start Example (Quickstart1.p2k)
xe "Quick Start Example"
Step  1  -  Initial Preparation
Step  2  -  System Layout
Step  3  -  Analyze System and Review Results
Step  4  -  Some Additional Simulations
See the Quick Start AVI’s (1-4) on the www.kypipe.com web site.

This will guide you through the complete layout development, data entry, and hydraulic analysis of a simple pipe network.  We recommend that you run Pipe2016 in as high a resolution as your monitor can display such that it can be comfortably read.  

Step 1  -  Initial Preparation
Initial steps include file selection, background preparation, and system data selections.

a.  File Selection - You can access an existing data file or create a new one.  In this demonstration we will create a new file.  Click on File (main menu) and select ‘New’.  The New File setup screen appears.  Select KYPipe.  
b.  System Data Selection – Go to the System Data [image: image241.png]


 (KYnetic) or System Data | Simulation Specs menu (Classic).  Select US Gallons per Minute for Units.  The default head loss equation (Hazen-Williams) and other defaults are all acceptable.  Click Okay.  Click [image: image242.png]


 (KYnetic) or on the ‘Map’ tab Classic) to return to the Pipe2016 map.

c.  Background Preparation - You can import a drawing or map image, utilize grid lines or choose not to use a background.  For this demonstration we will turn on a grid and use it to guide our layout letting Pipe2016 calculate pipe lengths.  

Click on [image: image243.png]


 (KYnetic) or Map Settings | Grids (Classic).  The default grid settings of 1000 (major) and 100 (minor) are good for our demonstration so we will use them.   Click on Major Grid and Minor Grid check boxes.  This will display background grid lines.  Return to the Pipe2016 map.

Step 2 - System Layout
The map area which appears on the screen will show a region approximately 1000 x 1000 feet with the 100-foot grid lines displayed.  This area will be appropriate for the demonstration.  A larger or smaller region can be displayed by clicking on the zoom in (+)  or zoom out (-) buttons on the left side.

[image: image244.png]Reservoir B
210 250

210 0

Reservoir A

a
200 30_ 200 210





Figure CE1 - 1  Example pipe system

The system we wish to lay out is shown above.  It is drawn on a 100-foot grid system.  It is a loop fed by Reservoir A (Grade (or HGL) = 300’) and discharges into Reservoir B (Grade (or HGL) = 250’).  The node elevations are noted at all junctions first.  This is followed by the reservoir grades at the two reservoirs.  The pipe material, diameter and roughness are noted for each pipe in a box.  Points (a) and (b) are shown for reference in the discussion below.  The development of the pipe system model is accomplished in three steps.

a.  Layout Pipes and Nodes - The entire piping system can be laid out using the mouse.  A right click (RC) adds pipes and nodes and a left click (LC) selects a node.  The following operations will produce the system layout:

1)  RC on gridline intersection to make first node  

2)  move mouse 300 feet (3 blocks) to right and  RC (a)  

3)  move mouse 200 feet up and RC  
4)  move mouse 200 feet right and RC  
5)  move mouse 200 feet down and RC (a)  
6)  move mouse 200 feet left (point to existing node) and RC  

7)  select node at (b) (LC) and move 100 feet up and 100 feet to left and RC

Now all the pipes and nodes are laid out.  Note all nodes are either junction or intermediate nodes and Pipe2016 has assigned pipe and node names.

b.  Change Node Types - Select any nodes which are different than shown and change to the correct node type.  To do this select the node and click on the Node Type description or in Classic click the drop down node list (Node Information Window below Name) and select desired type from list. 

1) Select node at Reservoir A (LC) and change node type to Reservoir (Grade type) 

2) Select node at Reservoir B and change node type to Reservoir (Grade type)

The system should now look as shown below.  

[image: image245.png]R-1

Pt





Figure CE1- 2  Completed pipe system layout
c.  Provide Data - Select each pipe and end node and provide data

1) Select each pipe and click Pipe Type (Pipe Info Window) and select choice from drop down list.  Select ductile iron (di) - 6 for pipe from Reservoir A and pvc - 4 for the rest.  Note that default roughness values are provided.  Provide appropriate Fittings Data (elbow for pipes with 90o bend, for example)
2) Select each Reservoir and provide values shown for Elevation and Grade (HGL).
3) Select each junction and intermediate node and provide Elevation.
d.  Save Data File - Provide a name and save your data file.  Click on File (Main Menu) and Save As and provide a file name in the popup menu, such as QS1 (for Quick Start example 1).  Note a copy of this file may be loaded by clicking the Examples button and going to the Class Exercises 1 folder.  It is called QuickStart1.P2K.
Step 3  -  Analyze System and Review Results
a.  Check Data and Run Analysis 
1.  Click Analyze (Main menu) and select Error Check.  If errors are flagged correct these.  If the message "No Errors" appears, proceed.  
2.  Click Analyze (Main Menu) and then Analysis.  In the Analysis Setup box, make sure Analysis Type ‘KYPipe’ is selected and ‘Use Current Year’.  Click Analyze.
b.  Review Results - The results can be reviewed on the schematic using Results Labels or by looking at the tabulated output.  

1.  Click on [image: image246.png]


 or Report tab and scroll through the tabulated summary of data and results.  Return to the Map.  
2.  Click on Labels (Main menu) and select Pipe Result A and Node Result A to show the results depicted in the Results Selection bar on the bottom right of the screen.  You can change the pipe (P) results (default is Flow) and the node (N) results (default is Pressure).  A helpful selection is Loss (head loss) for pipes and HGL for nodes because it provides a very useful view of the system operation. Printouts based on these selections are shown (Figure CE1-3 and 4). 

[image: image247.png]ODES Pressure

IPES Fiowrate

43.3

703>




Figure CE1- 3  Case 1 - Pressure and Flow


[image: image248.png]NODES HGL

PIPES Head Loss

300

i




Figure CE1- 4  Case 1 - Loss and HGL
Step  4  -  Some Additional Simulations (Quickstart2.p2k)
It is very easy to modify data and run a new simulation.  Several are described:

Age-Based Roughness – If the roughnesses are fixed, do the following:

Under [image: image249.png]


 Edit (Main Menu) click Select All Pipes.

Classic 

In the Edit Pipe Set box, under Item to Edit, select Roughnesses.
Under Operation select Not Fixed.

Click Proceed.

KYnetic
Click the “Roughness” row heading

In the window that appears, under Group Edit, select Unfix (Calculate).

Click Apply Edit

Rerun the analysis but this time uncheck ‘Use Current Year’ to remove that requirement and enter the year 2043.  The analysis now shows a significant change in pipe roughness due to aging and a substantial decrease in the capacity to transport water from Reservoir A to Reservoir B.  A printout showing flows and pressures illustrate this (Figure CE1-5). 


[image: image250.jpg]Nodes - pressure

Pipes - flowrate

5141

iy





Figure CE1- 5  Case 2 - Year 2023

b.  Add a Pump (QuickStart2.P2K) - We want to add a 40 HP (useful horsepower) pump in the line leading from Reservoir A about 100 feet from the reservoir.  To do this, click on (LC) the pipe at the desired location and click on Insrt (Pipe Information Window button) and select Intermediate Node.  Now in the map screen, select the intermediate node (LC on node) and change node type to Pump.  Select the pump and select Constant Pwr (power) for Pump Type and input 40 (HP) for the Power and 210 (ft.) for the elevation (Node Information Window).  These operations are shown in Figure CE1-6.  Now analyze the system and note the effect of this pump which provides around 136 feet of head and nearly doubles the flow.  A printout showing flows and pressures is shown (Figure CE1-6).

[image: image251.png]


[image: image252.jpg]Effcny% /75
—_
Pump Type
 TableC" File
@ ConsC Ratec
EJIE

Single



 
Classic

[image: image253.png]Elevation

itle
Parallel Singl¢

[Check Valve Lirary i Vave Pump -Rated
bion-Reopening Che Sprikerfesk Pump -Consta
[Bypass Line oAtz LErE




[image: image254.png]Node Type  Pump - Power

ame. Pump-1
Elevation 200

itle
Parallel Single
ICheck Valve X
hion-Reopening Che
IBypass Line
oV Time 0

Pover 4o
Eficiency % 75
Grade —




KYnetic
Figure CE1- 6  Case 3 – Adding a  Pump


[image: image255.png]7.3

NODES Pressure
PIPES Fiowrafe





Figure CE1- 7  Case 3 – Results - Added  Pump
QuickStart Example 2 – SI Units

[image: image256.jpg]Creating a
Network Model

Dr. Don J Wood and Dr. Srini Lingireddy
KYPIPE LLC, Lexington, KY, USA
www.kypipe.com




[image: image257.jpg]Laying Out Your Pipe
System
As Easy as 1-2-3

(1) Left Click (LC) to select existing node (or pipe)

(2) Select first node — move mouse and Right Click
(RC) to add Pipe and Node

(3) Select Node and use Dropdown List to change
Node Type




[image: image258.jpg]Step-by-step Network
Layout Example



[image: image259.jpg]Network Schematic

Junction Nodes

Reservoir Node demand

200m,200mm 300m,150mm

Elevation of all nodes = 100m

Depth of water in reservoir = 15m

Demand at all nodes = 500 Ipm

Pipes: DI pipes, Hazen William Roughness Coefficient = 120



[image: image260.jpg]Import KY.

AymiBE \ B
save

© Suge € Steam

© GoFlow © SwMM




[image: image261.jpg]File Edit View Analyze Labels Contours Cursornotatio

After previousstep....
K¥Pipe: cubic feet/sec Eq: HW
Map | Map Settings System Data | Other Data | Setup /

Simulation Specifications | Other | EPS (Extended Peric

Steady State System Data ‘ Sl

Specific Gravty [T
User Units | Units [cubic feet/sec

Friction Equation [Hazen Williams

Maximum # of Trials oo

Specific

User Units | U

o 5
CEU2Y | barrels hour



[image: image262.jpg]File Edt View Amshyre Lobels Contows Cursor Notstion _Facites Management_Tools _Help

After previousstep....

| Wap_ | Map Sotings [Sysism 0] othr Dt Satuptats | Ropor
‘Simation Spce | Other | 75 | Rpots| Prfrsces| Seatoeizrsuet | /
E e SystemTpe [7pe 7

spotc Gty | [Gomani Dot Sindor 1 S 2

i Exuson [FazerWiiams ]
Maximum # of Trials| ’z—n—
T —

¥ Mark Origin

vsarnts | s fiwsmn <] | | oo R ——

[ro File_Edit View Analyze Lsbels Contours CursorNotation Faciities Manager

Data | Setup/Defaults | Report |
Is | Emphasis/Contours | Legend |

‘Snap Al Now

DatalAnalysis
I~ Multiple Demand Types

I~ Check for NAN and INF-

™ View davics inets and

MapiLayout
I~ Reverse Arrow Buttons

I~ Do Not Save Previous Resuts
% Pan Method 2

I~ Use Old Toolbar

7 Use Vabe Cosficient (C)n
of Resistance (R) for Actve




[image: image263.jpg]Cciei

File Edit View Analyze Labels

LN
GAT]

Zal | ZwWin
Zsel | zPn
[

1lg

KYPipe:fters/min e HW
Map | Map Settings | System Data| Other Data | Setup/Defauits | Report |

Contours  Cursor Notation _ Facilities Management  Tools Help 1
glick

Empty

erid after previous step

T om0
e ————

e

RENERDN
e

Zar [ zwin
Zsur | zen

Leftclick g
Labels _Conto
K¥Pipe:fters/min Ez HW TableIndex  Noded
Map | Map Settings | System Data| Other Data|

Move cursor to any grid point

an @ lick — a junction
no

dew created as shown

/




[image: image264.jpg]Next step is to change junction node to reservoir node

File Edit View Analyze Labels Contour

K¥Pipe: lters/min Eq: HW Tble Index# Nod
Map | Map Settings | System Data| Ot

lﬁ
e

a
Zwin R1
B ]

i




[image: image265.jpg]Next step is to create a pipe and junction node 200m from reservoir node

Place cursor about 2 grid spaces from reservoir node an ick

R1 g ™ T

N

R-1 J-2

P



[image: image266.jpg]Repeat these steps to complete the layout process

ove cursor 3 grid spaces from junction node J-1 anick

R-1 J-2

N

2]

R1 J-2 - J-1

P2

Lotttk

P3

=

J-3



[image: image267.jpg]J-3

Now LEFT click on J-2 to select
that node first and then create

2 other pipes and nodes
B a 2 = o1
e
Rk
Gy V ﬁ \

@ - . 0,

LRT 9| o R 58 | s
44 s

e

P

P




[image: image268.jpg]Provide Data for Pipes and Nodes

!1I'This is where the beginners should use extreme caution on RIGHT and LEFT clicks !!!

b RIGHT click adds a new node and pipe. Accidental RIGHT click
can generate unwanted nodes and pipes. Sometimes the pipes may
overlay each other and the user may not see this easily.

Rk

@y L/

LEFT click is used for SELECTINGa node or a pipe

J-4

%QJ/

LEFT click on any pipe

P

Pipe Information

0w ord g G Coed K| K8/ A4
Mw,! Rot[Uset A | A ese

Nzll:e P-1 — |

Pipe Type|

Residential [§

ength|200, 4 K

|
‘Ltngm oo i Heters
Rougf v F

Fittings| ™ Closed |

Provide data



[image: image269.jpg]Provide Data for ALL pipes by selecting one pipe at a time

Rk
By Y
Next provide data for nodes:
4 - Com - o
; 4 a LEFT click on this node
LR o U | e s

% Nods Image
I Showon Map
Demand I~ Show All
mand_) |Lrge] Print| Move

Om Type[T <] | [ Fulll Load] Clear

0 ore gy [otac

= =
Name|[)-5 |

[Junction

Repeat these steps to provide
data for ALL nodes




[image: image270.jpg]Save the model before further processing.

* Edit View Analyze

New
Open,

Import KY Swerie

Import DT2 File il
Demat
Save

Directory: C:\...\KYPipe Doc

5 Users
&5 Publc
5 Documents
5 KrFipe Doss



[image: image271.jpg]Review Model Data:

File Edit View Analyze

Tabels [ @Bntours _ Cursor Notation

KYPipe:lters/min Eqt HW
Map | Map Settings |

Pipe Name.

Pipe it
(POt nd s e
Pipe Miterl nd Rting

Pipe Fitings
Pipe Results

Peak Velocity
Selected Pipe Labels
Pipe Labels Off

Node Name
Node Title
Node Elevation

Junction Demand and Type

Node Resuts
Seected Node Lol
Node Label Off
100 150: 120 100 100: 120
100 200:120 100 150: 120 100

2

100



[image: image272.jpg]Steady state analysis:

L
| Forward One Case Clanal ;; > Fow  ~]



[image: image273.jpg]View Results

File Edit View Analyze

Tebels ours_ Cursor Notation

Facilities Management  Tools Help.

KPipe: ters/min Eqt HW
Map | Map Settings |

[Tex(]

Pipe Name.
Pipe Title

Pipe Diameter and Roughness
Pipe Material and Rating

s €@

b

e @

Peak Velocity Pipe Resut B
lﬁ Seected Pipe Label: Pipe Resut A anl
Pipe Label Off Pipe Result Mifand Max
Al
100 100
sz s, Py

T __— PipeFlows (LPM)

100 o0 Joo. o498 4;/ A




[image: image274.jpg]File Edit View Analyze Labels Contours CursorNotation Facities Management Tools He

K¥Pipe: lters/min Eq: HW Table Index # Node:s
Map | Map Settings | System Data| Other Data | Setup/Defauits | Report |

I'—W
e

B
24

[E] L1

Pipe Results Type

Pipe Velocities



[image: image275.jpg]Fle Edt_View Anslyze

K¥Pipe: fters/min E HW
Map | Map Settings | €

[

a3 |
P
HZ'IAT

— o

rs_Cursor Notation _ Faciltes Management _Tools _Help

Pipe Name.
PipeTitle

Pipe Diameter and Roughness
Pipe Material and Rating

Pipe Fitings

Pipe Results

Peak Velocity

Selected Pipe Labels

Pipe Labels Off

NodeName
Node Title:

Node Elevation

Junction Demand and Type:
Node Results

Selected Node Labels
Node Labels Off

dl

20

Nodefjesult A
Node Result B
Node Resuit A and &

Node Results Type



[image: image276.jpg]Add a 20kW Pump

Junction Nodes

Reservoir Node demand

300m,150mm

Elevation of all nodes = 100m

Depth of water in reservoir = 15m
Demand at all nodes = 500 Ipm
Pipes: DI pipes, Hazen William Roughness Coefficient = 120



[image: image277.jpg]Left click on pipeline where the pump needs to be inserted

0| et
insr Rot L
Name [P

[ LA

Check Valve

Hydrant
On/Off Valve
Metered Connection
Intermediate Node

Residential [ Inline Meter

Meters
Ref
v [eo12

Pipe Title

ength[200 I~ F|

Rough[120 ™ F

Devicel

Device2

Fittings| [~ Closed

Resenvir

Reguiater

Loss Element

Presure Supply

Pump inserted on pipe P-1 Seiinkdedesk
Blowofi/Nozdle

ActiveValve

Vacuum Breaker




[image: image278.jpg]Left click on pump to select and edit pump data

Pump Type _Heb
Constant Power ~!

Device Data

CV Time[0
CV Res[0
Byps Res0

¥ Check Valve
I NonReopen CV
I Bypass Line

Wore Device Data
Pump Res[0

Node Title

leteTe




[image: image279.jpg]Display Flowrates and Pressure Heads

60.1 | .., 59.3

>

59.7

se Analyze






Class Exercise 2 – Water Distribution System (Example Base.P2K)
[image: image280.png]Reservoir





Figure CE2-1 Municipal Water System Layout

Description – Figure CE2-1 shows the basic layout for a drinking water distribution system. The water is supplied from a reservoir at a grade 120ft directly by a pump with the following head-flow pump characteristic data. An overhead storage tank is shown and has a water level of 250 feet.


Head(ft) 
Flow(gpm)


200
                    0


180
                500


150 
                800

The system is constructed of 6 inch ductile iron (red) and 4 inch pvc pipes and the roughness for new and 10-year old pipes are noted on Figure CE2-2. Key elevations are noted (1st number) and a scale (500 foot grid) is shown. A total demand of 600gpm is distributed at five nodes as noted by the figures (2nd number). These demands represent the average daily demand requirements.
[image: image281.jpg]- elevaton-—-1138 Y 120
13| =— _| §

WCE = 130(125)

EN

demand(gpn) \

-4 inch pvc

HWC = 140(135)

179 180





Figure CE2-2 Municipal Water System Data

                           [image: image282.png]



Figure CE2-3 Background Map (4500 feet wide)

Regular Simulation Exercises

 Carry out the following exercises using a data file called CE2map, which includes a background map file that is set to scale but no other data. This data file can be found in the File Open menu by Clicking on Examples button and browsing the Class Exercises 2  folder. Alternately you can open up a New file and import the background map (ce2map.bmp).  The may be found by clicking “Add Demo Map” in the Backgrounds menu. This map is not scaled. However, you can easily scale it by noting that the scaled distance from the SW corner to the SE corner is 4500 feet. To scale the map just lay out a pipe line from the SW to SE cornet and note the length on the unscaled map (Lmap). A scale factor of 4500/Lmap must then be entered for the Pipe Scale Factor (XY).  This is found in the Other menu  [image: image283.png]


 or System Data | Other tab.   Once you have a scaled background map the exercises below can be done.

a) Layout the piping system for this pipe network using the background map to locate the nodes and the map scale to set pipe lengths. When finished Click File | Save As and on the Save File menu under File Name provide a name for your data file (eg. Example Base.P2K) 
b) Provide data and analyze the network using the baseline data. The storage tank initial level (hydraulic grade) should be set to 250ft for this simulation. The results for pressures for the analysis of the baseline data are shown in Figure CE2-5. 
c) Replace the 600gpm demand by 600 residential meters, using as average residential demand of 1.0gpm each. Do this by indicating the number of meters on the pipe links, which connect the nodes with demand points. Divide the demand equally among the connecting pipes. For example, if 3 pipe links connect a junction node with a 90gpm demand, set 30 residential meters on each pipe link as shown below. Don’t forget to set the demand at the junction nodes to zero and the Average Residential Demand to 1.0 gpm  (Other menu  [image: image284.png]


 or System Data | Other). 
[image: image285.png]Other Data
Node 1

Node 2
12

[ [

Reverse

Residential
Meters 0

Rl
Voar ©




 [image: image286.png]


 [image: image287.png]


  
[image: image288.png]


   [image: image289.png]Map | Map Settings System Data | Other Data

Simulation Specs {Other \Eps | Reports | Pre

Pipe Scale Factor 00 [1

Pipe Scale Factor 7) [0

Average Residential Meter Demand




Figure CE2-4  Using Metered Connections for Demand Data
Results – The pressures for the baseline data with demands (b) are shown below. The pressures obtained using meters will be the same or very close to these values.

      [image: image290.png]



Figure CE2-5 Results for CE2 (b)

EPS Exercises

Extended Period Simulations (EPS) (example eps 24-hour.p2k, 2 and 3)
Setup and run the following EPS simulations.

EPS1 - Assume the tank is a 30ft diameter cylindrical standpipe with 260ft overflow (maximum) and 220ft bottom (minimum) elevations (hydraulic grades). The tank initially starts full at 8:00AM. Setup and run a 24hour extended period simulation using a demand pattern shown in the attached table. The pump stays on at all times.

EPS2 - Set up Change Data for the pump such that it is on when the GDF is >= 1.0 (hours 0-8 and 10-16) and off when the GDF < 1.0

EPS3 - Set up a control switch to turn the pump off when the level is 255 feet and on when the level is 225 feet.

EPS4 - Repeat the analysis EPS3 with the baseline demands increased by 50% 

	Actual Time
	Simulation Time
	Demand Mult. Fact.

	8:00 AM
	0
	1

	9:00 AM
	1
	1.1

	10:00 AM
	2
	1.2

	11:00 AM
	3
	1.3

	12:00 PM
	4
	1.4

	1:00 PM
	5
	1.5

	2:00 PM
	6
	1.3

	3:00 PM
	7
	1.1

	4:00 PM
	8
	0.9

	5:00 PM
	9
	0.7

	6:00 PM
	10
	1

	7:00 PM
	11
	1.3

	8:00 PM
	12
	1.6

	9:00 PM
	13
	1.65

	10:00 PM
	14
	1.4

	11:00 PM
	15
	1.1

	12:00 AM
	16
	0.8

	1:00 AM
	17
	0.4

	2:00 AM
	18
	0.2

	3:00 AM
	19
	0.2

	4:00 AM
	20
	0.5

	5:00 AM
	21
	0.7

	6:00 AM
	22
	0.8

	7:00 AM
	23
	0.9


Figure CE2-6  Demand Pattern for EPS runs  for CE2
     [image: image291.png]Ie)



  [image: image292.png]Map | Map Settings System Data | Other Data | Setup/Defautts | Report |
Simulation Specs | Other  EPS | Reparts | Preferences | Skeletonize/Subset |

Use EPS ¥
Total Time (hrs) [24 Starting Time (hrs 0-24) [6
Computational Peried (hrs) [1] Report Time Style [Miltary Time |

Report Period (hrs)





Figure CE2-7  Demand Pattern for EPS runs  for CE2

[image: image293.png]


  or Setups/Defaults | Demand Patterns [image: image294.png]Time/Change
Power Cost
Residential

Type 1

11

12

13

14

15

13

11

09

07

10

1

13



[image: image295.png]1

13

12

16

13

165

14

14

15

11

16

08

17

04

18

02

19

02

20

05

21

07

2

08

23

09




Figure CE2-8  Demand Pattern Setup for EPS runs  for CE2
[image: image296.png]Name[TANK-A I Fixed Diameter

Tank Diameter [30]

Elevation|120

e

My Level [250

———

Mn Level |20

——
Initial |250

———

Inflow|?
vl



[image: image297.png]Tank Fixed Diametei
TANK-A

120

0

0

250




Figure CE2-9  Overhead Tank Setup for EPS runs  for CE2
Setting up the EPS – Three steps are normally required for converting the baseline system into an EPS file.

1)  EPS System Data is required as shown in Figure CE2-7 ([image: image298.png]Ie)



 or System Data/EPS setup screen). The Total Time, Computational Period and the Starting Time should be specified. This setup calls for a 24 hour simulation using a one hour increment and the simulation start time is 8 AM. This time is chosen to coincide with the Demand Pattern shown in Figure CE2-6.

2)  The Demand Pattern data is entered on the Demand Pattern screen ([image: image299.png]


 or Setups/Defaults | Demand Pattern) as shown in Figure CE2-8.

3)  Tank Data must include the Maximum, Minimum and Initial levels as well as either a tank diameter or a volume and shape ID as shown in Figure CE2-9.

[image: image300.png]Node Changes

o conf

Time/.
o Value

6 CClose A
10 OOpen

16 CClose



[image: image301.png]Changes for PUMP-1

Time [Change Valie
5 Closed Chose.
i) Open Open
e Closed Chose.




Figure CE2-10  Pump Changes for EPS2 - CE2

EPS Results
EPS1 – The EPS1 simulation can now be run. This run considers a situation where the pump is operated continuously for the entire 24 hour period. (Example EPS 24-hour.P2K)
EPS2 – Change Data is added for the pump to turn the pump off whenever the Global Demand Factor (GDF) is less than 1. This occurs from hours 8-10 and 16 – 23 and the Change Data screen for the pump is shown in Figure CE2-10. The results for EPS1 and EPS2 are shown in Figure CE2-11 which compares the two cases. Note the Pipe2016 capability to show a Previous Result is very useful for comparing cases such as these.

The upper trace is for EPS1 where the pump operates continuously and the tank is filled and will be shut off from hour 20 on. (Example EPS 24-hour2.P2K)

EPS3 – This illustrates the use of a Control Switch to control the on/off status of the pump. The pump turns on when the HGL level drops below 225 feet and turns off when the level exceeds 255 feet. The setup for this device is shown in Figure CE2-12 ([image: image302.png]Ie)



 - [image: image303.png]R, contro Switches



 or Other Data/Control Switches). The tank level for this situation is shown in Figure CE2-12. This plot shows that the pump turns off at around 18 hours into the simulation. (Example EPS 24-hour3.P2K)
[image: image304.png]260

250
)
G 240
I

230

220

Level in Storage Tank - CE1-EPS1 - EPS2

5 10
time (hours)

15

20

25




Figure CE2-11  Overhead Tank Level for EPS1 & EPS2  for CE2
[image: image305.png]Map | Map Settings | System Data Other Data | Setup/Defaults | Report |

Control Switches | Canstraints | Calibration | Qualiy | Quaity Calibratian | Meters | Library Elements | Active

Switch Units [HGL (t or m)

controlled | T on sensing below/ | low on high
is when and when | above
element off node between | level off level

PUMP-1  is on  when TANKA s below 205 and off  when above 255]





Figure CE2-12  Control Switch Setting  for EPS3
[image: image306.png]Level in Storage Tank - CE1-EPS3
260

255
250
245

)

% 240
235
230
225
220

0 5 10 15
time (hours)




Figure CE2-13  Overhead Tank Level for EPS3
Surge Exercises
 Set up and carry out the following surge analyses 
Surge1 (Example Surge Rapid Shutdown.P2K)-  A rapid rundown of the pump following a power outage. Utilize the Baseline demands and tank level and consider the both Fixed Demands and Pressure Sensitive Demands.
Surge2 (Example Surge Compressor Tank.P2K) – Repeat Surge1 with closed compressor surge tank attached just downstream from the pump. The surge tank has a 4 foot long 6 inch connection with one elbow and the compressor is designed to maintain 50 cubic feet of air while the pump is operating. Utilize the results of this exercise to size and precharge a bladder tank which will perform comparably.
Surge 1 Setup (example surge rapid shutdown.p2k)
Setting up the Surge Analysis – With some minor changes your baseline data file can be modified to carry out a surge analysis. The following steps are required.
The System Type must be changed to Surge and additional System Data provided. Figure CE2 – 14 shows this screen. The Total Simulation Time should be specified and for this exercise a 60 second simulation is specified. 

The wave speed for the pipes must be defined. For this exercise two types of pipes are modeled. The 6 inch ductile pipe has a wave speed of approximately 4000 ft/sec. and 1500 ft/sec for the 4 inch pvc pipe. These wave speeds are set by using 1500 ft/sec as the Default Wave Speed as shown in Figure CE2-14. All pipes will automatically be assigned this value if the wave speed is not specifically defined for a pipe. Using Pipe2016’s Global Set selection and editing capabilities the wave speed for the ductile iron pipes are set as shown in Figure CE2-15. All 6 inch pipes are selected as shown and the Wave Speed for this group set to 4000 ft/sec as shown. All others will be set to the 1500 ft/sec. (default) and this value will appear in the Pipe Data box as shown in Figure CE2-15.

  Change Data is required to define the cause of a transient event. For this case a 2 second rundown for the pump is set up as shown in Figure CE2-16. This data specifies that the pump run at full speed (speed ratio = 1.0) for the first 2 seconds and then ramp down to zero in the next 2 seconds. It is recommended that the initial steady state conditions be maintained for a short period (as this does for 2 seconds) to verify that the system steady state is being maintained prior to the start of the transient. Also, as shown in Figure CE2-16 if not done previously a check valve should be specified for the pump if this device is present to prevent reverse flow. Without a check valve flow will reverse through the pump when the speed is reduced. 

[image: image307.png]Simulation Specs | Other | Reports | Preferences | Skeletonize/Subset |

Surge System Data SystemType [Suge v

Specific Gravty [1 Additional Data
User Units | Units [GPh Demand Calcul
o Fixed Demands. ~
Equation |Hazen Williams
Length Accuracy [50
Total Simulation Time [50]
Wave Speed
Cavitation Head Atribute used for pipes "Wave Spee
Time Step nerement| [wavespecs <]

Default Wave Speed [1500




Figure CE2-14  System Data / Simulation Specs – Surge1
[image: image308.png]Edit Pipe Set || _Set Selection
Pipe Status Diameter <]
Conen ot ||
o

e to Edit i
wave speed [
Operation
New Val

At New Set

Value [4000] Add To Set

Select from Set

Proceed (seciom o8t |
———||| Remove fiom Set




 
Classic – Select all 6 inch pipes, then edit Wave Speed

[image: image309.png]Pipe.
Name
IPipe Type

/ave Speed
ILength
IRoughness
Fittings
[First Node
[Last Node
cssenaicrs

Group Selection and Editing: |

Group Edit

ductile -6
pve-4



 
KYnetic – Select 6 inch pipes   
[image: image310.png]Name

Pipe Type
ave Speed i

Length

Roughness

Fittings

First Node

Last Node

Residentl liters.

nstall Year

Group Selection a

Group Edit

Edit Type
© Fix

® alculate)
& NewVaie,
© Add

© Multiply

A
K

e

[Temperature

Value [4000

v Apply Edit





KYnetic – Edit Wave Speed

[image: image311.png]Name [23

Pipe Type

Diam

Mirl Jpve

wy Spd [1500 -]

Length[ggs

Rough [140




[image: image312.png]fName: 23

PieType -4 P
ave Speed 1500

ength g
Roughness 140
Fittings

FistNode 12
LastNode 19
JResidential lieters 0

nstall Year 0

W 7
=6 S





Figure CE2-15  Defining Wave Speed – Surge1

[image: image313.jpg]Device Data
CV Time[0.01
oV Res D1

Byps Res|D

!’ Check Valve
NonReogen CV
V' Bypass Line



[image: image314.png]Node Type  Pump - Table.

hiame PUMP-1

lovatid]_Clickto
|Group Edit

itle

Paralel Single

D i

ICheck Vaive X

hion-Reopening Che

IBypass Line

oV Time 0.0

[CV Resistance 0.1

I5ypass Resistance )





Additional Pump Data

[image: image315.png]Node Changes

o conf

Time/.
Case

Value




[image: image316.png]Changes for PUMP-1

[rime

[Change

Valie

Speed ratio
speed ratio
speed ratio

1

1

o




Pump Rundown Data
Figure CE2-15  Defining Pump CV and Changes for Rundown – Surge1

Surge 1 Results – The pressure vs time plot for the dead end node (right side of system) is shown in Figure CE2-17. The blue trace is the result for Fixed Demands. When demands are fixed they remain constant even when the pressure is reduced. Pressure Sensitive Demands vary with pressure and will be reduced as the pressure goes down. This will have a very significant effect on the pressure transient. This option is implemented on the [image: image317.png]


 or System Data/Simulation Specs screen as shown on Figure CE2-16. The same result (pressure at the dead end) is shown as the red trace on Figure CE2-17 using Pressure Sensitive Demands. 

                                        [image: image318.png]Demand Calculation

Pressure Sensitive

Exit Head [0

Do not caleulats mtrusion





Figure CE2-16  Defining Pressure Sensitive Demands – Surge1
[image: image319.png]Head at dead end (fixed and pressure sensitive demands)

P

20 30 40 50
time (sec.)

60




Figure CE2-17  Results With Fixed and Pressure Sensitive Demands – Surge1

Surge2 Setup (example surge compressor tank.p2k)  – A compressor Surge Tank is added just downstream from the pump as shown in Figure CE2-18. This tank is operated such that 50 cubic feet of air is maintained under the initial conditions. The required data is shown in Figure CE2-18. The Tank Volume does not directly affect the surge analysis. The Inflow and Outflow Resistances will normally be the same and depend on the characteristics of the connection. A Pipe2016 : Surge tool is provided to calculate the resistance for a tank entrance and the use of this tool is illustrated in Figure CE2-19.  The schematic and diagram shown in Figure CE2-19 indicate that a 6 inch connection resistance is approximately 1.0 and the actual calculations verify this value.

[image: image320.png]


  [image: image321.png]


[image: image322.png]Node Type ~ Vert Closed Surge:

IName SDO-1
Elevation 9%
itle

Infow Resistance 1
Jouttow Resistance 1

ank Volume 100



 
Figure CE2-18  Adding a Closed (Compressor) Surge Tank – Surge2
[image: image323.png]ction to Tank

Typical Dismeter vs. Resistance Plt

lameter vs. Resistance

100
BIAN
Tank g \\
-
% oo
Comnecting Pipe| oo
ogo0n
L o 0 = @

Elow iameter (in)




                                    [image: image324.png]=~ Resistance Calculation Tool

Uit [Engish

Caloulate Resistance From [Connacton to Tark.

No.of ebows [
Fipe Diameler |5 in

Lengthof Ppef4

AddtonalKs [T5
Ficton Factor) [3.02

Compute Resistarce.

Resistance = [.§7205856%8




Figure CE2-19  Resistance Tool – Tank Entrance – Surge2
Surge2 Results - Figure CE2-20 compares the pressure plot at the dead end with and without the surge tank. For this comparison the Fixed Demand option is used.

Sizing Bladder Tank – The results of the analysis using a compressor vessel can be used to size and precharge a bladder tank which will provide the same response. A tool is provided to do this. Three data items are needed to use the tool:  the initial air volume, the maximum air volume, and the initial head at the tank.  The initial air volume was input so we know this value. A plot of air volume shown in Figure CE2-21 shows the maximum air volume is 71 cubic feet and the initial line head is calculated by the initial steady state analysis. This is shown in the Surge Report (Figure CE2-22).

[image: image325.jpg]Pressu

re at dead end (with and without surge tank)

20 30 40
time (sec.)




Figure CE2-20  Results With and W/O Surge Tank (Fixed  Demands) – Surge2

[image: image326.png]7 Volume of Air in Surge Tank

70
68
66
64
262
2 60
>58
56
54
52
501
48

0 10 20 30 40
time (sec.)




Figure CE2-21  Air Volume – Compressor Surge Tank – Surge2

[image: image327.png]SURGE PROTECTION DEVICE DATA

Resistances
Pos. Pos.  Ext. (Diameters) Line  Iintial - Surge Tank Data -
#1 42 Pos. our I Head Flow Total Vol Ini_Gas Vol

sD0-1 s 100 100 189.12  0.00 100.0 so.0




Figure CE2-22  Surge Results – Initial Head at Surge Tank– Surge2
[image: image328.png]Pipe2000 - Bladder Tank (CopyRight: KYPIPE LLC 2004)

Unis
& Engish ca Masinum AitVolume [77
s Iniial i Pressure [fgg
 Galons & Cubio Feet Iniial it Volume 55
Pressue
© psl e Frecheige Pressure

Bladder Volume
Flatm) = 3382t or 147 psi

Platm) = 10.34m or 101.435kPa Close.




Figure CE2-23  Bladder Tank Size and Precharge  Tool – Surge2
The Bladder Tank Tool shown in Figure CE2-23 calculates the size (85 cubic feet) and precharge (97 ft.) required for a Bladder Tank which will perform the same as the compressor vessel. This is easily confirmed by changing the closed surge tank to a bladder tank with the above characteristics.
Water Quality Exercises
WQ1 (Water Age in Tank 25%.P2K): This example illustrates the use of Pipe2016-EPANET program to compute water age at different locations in the distribution system. Assume that the tank is almost full at time 0 (say 259.7 ft) and that the tank level returns to the same level at the end of 24 hours after a 25% turnover (that is the tank level drops to about 250ft).  Set up and run an EPS analysis to reflect this condition. This analysis requires a control switch on the pump and the required control switch setup is shown in Figure CE2-24. In addition, the pump speed setting should be changed to 0.976 in order to bring the tank level back to where it originally started. Figure CE2-25 shows the pump speed setting screen with the pump speed ratio set to 0.976. 
[image: image329.png]Ie)



 - [image: image330.png]R, contro Switches



 
[image: image331.png]Map | Map Settings | System Data Other Data \ggmp/omus\ Report |
Control Switches | Canstraints | Calibration | Quality | Quality Calibratian | Meters | Library Elements | Activ

Switch Units [HGL (t or m)

controlled |, Ton g [ below | low [ Ton [ T T high
element off node between | level | ™" off ? level

PUMP-1 s on when TANK-A s below 250 and off  when above 259.7





Figure CE2-24.  Control Switch Setting for WQ1
[image: image332.png]JUMP-



  [image: image333.png]Node Information.

et o] g ata g Cony A £ &

T Less) <y Rt ser ry
Name[PUMP-1 ‘D’ij
Pump Head| Flow Efi%

Elevation %2

e — ) 5nn

Sp Ratio[D976  |[150 800

— — o o




[image: image334.png]lcV Time 0
ICV Resistance 0
5 ypass Resistance )
ISpeed Ratio  0.976

lPup Resistance 0

Direction =




Figure CE2-25. Speed Ratio Setting for Pump-1 (for WQ1)
Once the model is set up to run with its tanks starting and ending at the same level during the specified time period (typically 24 hours), it can be used to compute water ages at different locations of the system.  Access the water quality screen ([image: image335.png]


 - [image: image336.png]Water Quality Menu



 or Other Data | Quality screen) and provide a total simulation time of 500 hours, a water quality computational time of 0.1 hours, age of 1 hour for the reservoir R-1.  Figure CE2-26 shows the corresponding water quality data screens. Run the water quality analysis with an option to load results for the entire simulation period (500 hours) but load very 10th set of results (Figure CE2-27). 
[image: image337.png]Qualty Simulation Time (500
Time Units [Hows 7]

Quality Time Step 01
Qualty Parameter [Age 7]
S



        [image: image338.png]Reservoir Source Data

Resel

Age Patt





Figure CE2-26. Water Quality Data Screens for WQ1
[image: image339.png]Analysis Year

R Use Curtent Year

—

Analyze

Cancel

I™ SortNumerically (slower)

Analysis Type
© KPipe

 Water Quality (EPANET)
€ Hydraulic Calibration

 Rural Analysis

€ Fireflow and Hydrant Analysis

€ System Head Curves

I~ Report Shows All Flow

I™ [BEUE Ssiei Bafoie ARaRsTE

Load [every 10th setof results. Load allmes




Figure CE2-27. Analysis Setup for WQ1
Figure CE2-28 shows the water age in TANK-A during the 500 hours simulation. As the tank was exercised only by about 25%, the net age of water continues to increase and eventually stabilize around 120hours. 
[image: image340.emf]0 100 200 300 400 500

Time (hours)

-20

0

20

40

60

80

100

120

140

Age (hours)

Age of water in storage tank 


Figure CE2-28. Age of water in storage tank (WQ1)
WQ2 (Water Age in Tank 75%.P2K): This example is the continuation of the previous example illustrating the impact of about 75% turnover in tank level on the age of water in the tank. Figure CE2-29 and 30 illustrate the data screens for this analysis and Figure CE2-31 shows the water age graphs for TANK-A. 
[image: image341.png]Ie)



 - [image: image342.png]R, contro Switches



 
[image: image343.png]Map | Map Settings | System Data Other Data | Setup/Defautts | Report |
Control Switches | Canstraints | Calibration | Quality | Quaity Calibration | Meters | Library Elements | Activ

Switch Units [HGL (t or m)

controlled |, Ton sensing [ T below! | Tow [ Ton/ [T 0 T high
element off node between | level | ™" off ? level

PUMP-1  is on when TANK-A is below 230and of when above 259.7]




Figure CE2-29.  Control Switch Setting  for WQ2
[image: image344.png]el Wre g [Dta Chng Copy A | £ &4
o Less, ey ot User ry

Name[PUMP-1 of
Pump ~ ||| Head| Flow Ef%
Elevation %2 o

+r———— ||180 500

Sp Ratio1 01 150 800

——r—— o T
0 0




[image: image345.png]ICV Resistance 0
5 ypass Resistance )

ISpeed Ratio 101
ump Resistance 0

Direction

-




Figure CE2-30. Speed Ratio Setting for Pump-1 (WQ2)
[image: image346.emf]0 100 200 300 400 500

Time (hours)

-20

0

20

40

60

80

100

120

140

Age (hours)

Age of water in storage tank 

New Prev 

 
Figure CE2-31. Age of water in storage tank(WQ2)
WQ3 (Water Quality Chlorine.P2K): This example illustrates the computation of residual chlorine concentrations in the distribution system. Use Water Quality Chlorine.P2K model and provide necessary additional data as shown in various figures of this section to perform residual chlorine analysis. Use a wall reaction rate of -0.8/day and bulk reaction rate of -1.25ft/day and a first order decay rate for all reactions. Figure CE2-32 shows the water quality data screens along with the necessary data. An initial concentration of 2mg/l (ppm) for the tank (TANK-A) and a concentration of 2.5mg/l for the reservoir (R-1) are assumed. Complete mixing of water is assumed for the tank and the data is specified by selecting the “Mixed” option for the mixing model. 
[image: image347.png]Global Bulk Reaction Rate [125 Qualiy Simulation Time [0

Global Wall Reaction Rate [08 Time Units [Hows 7]
Order of Reaction - Buk [1 ] Quality Time Step 01 Update Ta
Order of Reaction-Wall [ ~|  Quality Parameter [Chernical +] o

Order of Reaction - Tank [1 ~|  Chemical/Tank Name [Chiorine
Uimiting Potential 0 Atribute used for nodes Initial Concentration” Initial Conc

Roughness Corrrelation |0 Attribute used for nodes "Initial Age" | Initial Age
Quality Tolerance |0 Attribute used for pipes "Bulk Reaction Rate"|Bulk Rate

Difiusivity (sqr ftfsec) [1.3E-8 ~|  Attribute used for pipes "Wall Reaction Rate" |Wall Rate




[image: image348.png]Tank Source Data

Tank nitial Concentration Pattern |Bulk Reaction RateMixing Model Volume
TANK-A 2 Mixed I |





[image: image349.png]Reservoir Source Data

Res¢ al Conce





Figure CE2-32. Water Quality Data Screens for WQ3
Figure CE2-33 shows the residual chlorine concentration at one of the tail end nodes (node 20) during the last 50 hours of the simulation. 
[image: image350.emf]450 460 470 480 490 500

Time (hours)

0.0

0.2

0.4

0.6

0.8

1.0

1.2

1.4

1.6

1.8

Chlorine Concentration (mg/l)

Node 23


Figure CE2-33. Residual Chlorine Concentration at Node 23 (WQ3)
WQ4 (Water Quality Trace.P2K): This example illustrates tracing percent contribution of water from a specified source (tank or reservoir) to different part of the network. In this example, the percent contribution from TANK-A to different parts of the network are computed. Figure CE2-34 shows the water quality data screen for this example. 
[image: image351.png]Qualty Simulation Time 24
Time Units [Hours =]

Quality Time Step 01
Quality Parameter [Trace =]
ChemicalTank Name [TANK-A




Figure CE2-34. Water Quality Data Screen for WQ4
Figure CE2-35 shows the plot of percent contributions from TANK-A to node 13 over a 24-hour period. 
[image: image352.emf]0 5 10 15 20 25

Time (hours)

0

20

40

60

80

100

Percent Contribution

Node 13


Section 3 – Training Exercises
Training Exercise #1 – Industrial Water Distribution System 
Description - (Industrial Base.P2K) the schematic shown below in Figure T1-1 represents a water distribution system for a large industry. It is fed from a large city water main. The pressure in the main will vary with the flow removed.  A fire flow test on a nearby hydrant gave an 80 psig static pressure and a residual pressure of 69.6 psi at a flow of 3600 gpm. The water tower is for fire protection and the elevation of the connection is 100 feet. The line length, diameters, node elevations, and normal demands for the industry are shown on the schematic. Two valves are shown with data for the valve characteristics. Carry out the following steady state scenarios. 

· 1. Prepare the model and data and analyze the system for the demands shown. 

· 2. If the storage tank is full the valve leading to the tank will close thereby eliminating flow to the tank. Modify the data file created in part 1 to simulate altitude valve closure. You may accomplish this by 

· A. Closing one of the pipes leading to the tank

· B. Closing the tank (use on/off button in the node information window) 
· C  Closing the Globe Valve
· C. Use “Node Changes” menu to close either of the elements – valve, pipe, or tank

· 3. Peak demands of 150% normal are expected. Analyze the system (with the globe valve open) for peak demands.

·  4. Change the diameter of the 680-foot line to 10” and analyze the system with normal and peak demands.

· 5.  Repeat case 4 with the Butterfly Valve set to 50% open.

· 6. Use Change Data to set up the 6 cases described above. 

[image: image353.jpg]Elevation — gg 1000 - Demand

Diameter —
Static Pressure = 80 psi Length -

Pres. = 69.6 psi @ 3600 gom

8
2

90

12 : 450

Cv = 1050
Butterfly valve

HWC = 120
(ductile iron)

K=64
globe valve




Figure T1-1 – Industrial Water Distribution System

Creating the Model -note that the network layout is presented as a “not to scale” schematic picture. Therefore the system can be laid out to represent the arrangement shown in Figure T1-1 but lengths will be entered and not scaled from the layout. The system contains two valves, a tank, and a connection to a supply with variable pressure (Variable Pressure Supply).

Model Data – The two valves require either a Resistance (R) or Valve Coefficient. A tool is available to use the data provided to determine the resistance for the 100% open valve. The use of this tool and the Data Boxes for the 2 valves, tank, and Pressure Supply are shown below. The data entry is straightforward. Note that the only additional data required for the tank is the Initial Level (250 feet). Max and min levels are not needed because we are setting up a regular (steady state) simulation and the level stays constant.

[image: image354.png]Resistance Calculation Tool

Unit[Engish <]

Caleulate Resistance Fiom [Vinor Loss Cosficients
Minor Loss Coeffcent [57

Fipe Diameler |5 in

Compute Resistarce.

Resitance = [25314003514




Resistance Calculator Tool, R for Globe Valve
[image: image355.jpg]Init Ratio|!
sl

Valve Type

=



[image: image356.png][CV Resistance 0
5 ypass Resistance )

Grade. —

Direction =
fon/oft v

Resistance 100% 26
Initial Ratio 1
alve Type  Globe




Active Valve Data

[image: image357.png]Name[TANK-§
Tank

Elevation 100

e
Mix Level
—
Mn Level |9
—
Initial [250

—

Inflow
L



[image: image358.png]Tank Variable Diam

TANKB
250

0

0

250




Tank Data
[image: image359.png]. Pipe2000 - Resistance Calculation Tool (...

Unit[Engish  ~]

Caloulate Resistance From [Fiow Cosficents
Flow Cosffiient [1050 Flow in gom at 1psi drap

Speciic Graviy (6)]7

Compute Resistarce.

Resistance = [0.4217170060





Resistance Calculator Tool, R for Butterfly Valve
[image: image360.png]


 [image: image361.png]Bypass Resistance )

Grade

Direction =
on/oft v

Resistance 100% 042

Inital Ratio 1
alve Type  Butterfly




Active Valve Data

[image: image362.png]Name[vP-1
Pressure Suppl «|

Elevation 100
——

Gage Dif
el

Static Pr|30

—
Res Pr/59.6
—_

Res Flow|3600
—_

¥ Rated




 [image: image363.png](Gage Diference 0
IStatic Pressure 50

Residual Pressure 696
IResidual Flow 3600
IMain Supply X




Pressure Supply Data
Figure T1-2 – Use of Tool and Node Data Boxes – Exercise T1
Training Exercise #1 – Regular Simulations

Regular Analysis Results (Industrial Base.P2K) – The baseline model was set up and two cases were run. 

1) Case 1 – both valves fully opened

2) Case 2 – the globe valve is closed

The flowrates (gpm) and pressures (psi) for Cases 1 and 2 (globe valve closed) are shown in Figures T1-3 and T1-4.
[image: image364.jpg]



Figure T1-3 – Results Case T1-1 

[image: image365.png]



Figure T1-4 – Results Case T1-2 – Globe Valve Closed
Using Change Data (Industrial Changes.P2K) – For item 6 you are asked to prepare data for all 6 simulations using the “Node Changes” menu. Remember that except for system demands, the changes made for previous runs define the system characteristics prior to the next run and it might be necessary to include data to change the parameters back to their original values. The following cases are to be set up.
Case 0 – Baseline data

Case 1 – Same as 0 with globe valve closed

Case 2 – Globe valve opened and Global Demand Factor (GDF) of 1.5

Case 3 – Same as 2 with 680’ pipe (pipe 7) diameter = 10 inches (GDF = 1.5)

Case 4 – Same as 3 with GDF = 1.0

Case 5 – Same a 4 with butterfly valve setting = 0.5
These Changes require a Demand Pattern setup to define the GDF’s and several Change Data Boxes for the Node and Pipe Changes. These are shown below:
KYnetic Demands menu icon: [image: image366.png]



[image: image367.png]Map | Map Settings | System Data | Other Data Setup/Defaults | Report |
Pipe Type | Fittings | SlidersPrecision | Change Pattems {Demand Paiterns

Load | Save | Clear Cases [4

Pattern Name |untitled

Global Demand Factor |1
ime/Change 1 2 3 3 5 O
Power Cost

Residential

Type 1 1 15




Figure T1-5 – Demand Pattern - Case T1-Changes

Note the Demand Pattern is accessed with [image: image368.png]


 or Setup/Defaults/Demand Pattern and entries left blank apply the last factor to the Demand.  Also for this example all demands are Type 1. The 3 Change Data boxes required for this analysis are shown below.  Note that the diameter change for the pipe applies to subsequent cases unless a new value is specified.
[image: image369.png]Node Changes

o

Time/.
Case

Value




[image: image370.png]Changes for AV-1

[Change

[Value

Rato

05




Case 5 -  Butterfly Valve

[image: image371.png]Node Changes

o

Time/.
Case

Value




[image: image372.png]Changes for AV-2

Valie

05

7T

o




Case 1 and 2 – Globe Valve 

[image: image373.png]Pipe Changes

o o]

Time/.
Case

3 bio

Value




[image: image374.png]Changes for 7

Valie

0




Case 5 – 680 ft. pipe
Figure T1-6 – Change Data - Case T1-R6 – Exercise T1

[image: image375.png]


[image: image376.png]e
aa
a8
a4
w50
s
s
s
055,

Ex
Ex
73
s
w02
s
a1
s
02




Figure T1-7 – Results for Multiple Simulations (Table) - Cases 0-5 – Exercise T1

[image: image377.png]Pressures (psi)

=)

Case

o





Figure T1-8 – Results for Multiple Simulations (Plot) - Case 0-5 – Exercise T1

Results for Multiple Simulations (Industrial Changes.P2K) – One advantage of setting up multiple simulations instead of several single case runs is that the results can be presented in a single table or plot as shown above for this exercise. Pressures for the two selected nodes are presented in a table (Figure T1-7) and plot (Figure T1-8) as shown.

Training Exercise #1 – Extended Period Simulations (EPS)
(Industrial EPS1.P2K)  The schematic shown in Figure T1-1 represents a water distribution system for a large industry. It is fed from a large water main and the pressure in the main will vary based on the supply data provided. The water tower is for fire protection. Normal demands for the industry are shown on the schematic. The tank has the following characteristics:

Tank Details: Overflow elevation = 220ft, minimum elevation = 180ft, tank diameter = 30ft. 

Setup and carry out the following EPS runs:
EPS1 (Industrial EPS1.P2K)   - A 24-hour EPS using 1-hour computational intervals for the following demand multiplication factors, assuming that the tank is initially half full at 200ft. 

· 0-8 hours, factor = 1

· 8-16 hours, factor = 1.5

· 16-24 hours, factor = 0.5

EPS2 (Industrial EPS2.P2K) - Add a 70 (useful) horsepower booster pump parallel to line 1. This pump will turn on when the water level in the tank drops below 190ft and will remain on until the water level exceeds 210ft. When the pump is off the pressurized supply directly feeds the system. Assume the booster pump is initially off with the water level in the tank at 200ft.  Carry out a 24-hour simulation using a 1-hour computational interval with the same demand pattern as above.

EPS Data – To convert from a Regular Simulation to an EPS it is only necessary to access the EPS Data ([image: image378.png]


 or System Data/EPS) and provide the Total Time and Computational Time Period. In addition the Tanks must include a Maximum, Minimum level (in addition to Initial Level) and either a Diameter or Volume and a volume/depth table. Although not required, a Demand Pattern will often be needed to define changes in demands over the simulation. This data for Exercise T1 is shown in Figure T1-8.

If a Control Switch is needed to control pump or valve operation such as for EPS2 then additional data such as that shown in Figure T1-11 is required. To accomplish the desired control a pipe with the pump must be added as shown in Figure T1-11 to model the action when the pump is on. When the pump is on the valve will be closed and vice versa.

EPS Results (Industrial EPS1.P2K, Industrial EPS2.P2K) – Results are shown in Figures T1-9 and T1-10 for EPS1 when no booster pump is utilized. For this case the tank completely empties after 11 hours resulting in very low pressures. With a booster pump turned on by a control switch the tank does not empty pressures do not get as low. Figures T1-12 and T1-13 show these results.

[image: image379.png]Namef[fY&E  ||@ Fixed Diameter
Tank 71| |Diameter 30

Elevation 100

—_—

My Level [220

——

Mn Level|180

_——
Initial |200

———

Inflow|?

P




[image: image380.png]Tank Fixed Diametet

IName TANKB
Elevation 100
MaxLevel 220

IMin Level 180
intial Level 200
inflow

itle





Tank Data

[image: image381.png]


  [image: image382.png]Simulation Specs | Other [EPS | Reports |

Use EPS ¥

Total Time (hrs) [24

Cormputational Period (hrs)

Report Period () [

Default Power Cost (§/kwhr) [

Intermediate Reports [~




EPS Input
[image: image383.png]



[image: image384.jpg]ime/Change
Power Cost

Residential
Type 1

Type 2



[image: image385.png]e/Changé

Power Cost

Residential
Type 1
Type 2

[

15

10

1

12

3

[

15

16

05




Demand Pattern
Figure T1-9 –  EPS Data – Exercise T1-EPS

[image: image386.png]HGL (1)

225
220
215
210
205
200
195
190
185
180
175

Tank Level - no control switch (T1-EPS1)

10
Time (hours)

15

20

25




Figure T9 –  EPS Results – Exercise T1-EPS1

[image: image387.png]Pressure at Dead End - No Control Switch

5 10 15
Time (hours)

20

25




Figure T1-10 –  EPS Results – Exercise T1-EPS1

[image: image388.jpg]



[image: image389.png]Ie)



 - [image: image390.png]R, contro Switches



 
[image: image391.png]Control Switches | Canstraints | Calibration | Quality | Quaity Calibration | Meters | Library Elements | Active

Switch Units [HGL (t or m)

controlled | T on sensing || below/ | low on high
is when is and when | above

element off node between | level off level

Pump-1  is on when Tank-B is below 190 and off  when above 210

|Av- is off when Tank-B s below 190 and on  when above 210)




Figure T1-11 Control Switch Model (pump initially off) and Data – T1-EPS2

[image: image392.jpg]Tank Level with Control Switch

o

10
Time (hours)




Figure T1-12 –  EPS Results – Exercise T1-EPS2

[image: image393.jpg]Pressure (psi)
(o))
o

Pressure at dead end with Control Switch

o

10
Time (hours)




Figure T1-13 –  EPS Results – Exercise T1-EPS2

Training Exercise #1 – Surge Analysis (Industrial Surge.p2k)
1) Surge Analysis - Modulating Regulating Valves – Training Exercise #1
Problem description (Industrial Surge.P2K) - Set up and carry out a 30-second surge analysis to determine the pressure increase due to a rapid (2-second) rejection of the 1200 gpm discharge. The principal additional data required is the wave speed in the pipes and a description of the cause of the transient.

[image: image394.png]Setup and Run 30 second Surge Analysis

Wave speed = 4000 1/s (ductile)

Shutdown 1200 gpm
flow in 2 seconds




Figure T1-14 –  Surge Analysis Conditions – Exercise T1-Surge
KYnetic System Data menu icon: [image: image395.png]



[image: image396.png]{Simufation Specs | Other | Reports | Preferences | Skelstonize/Subset |

Surge System Data SystemType [Swge ]
f Additional Data

Specific Gravity

Joer rits | Unite [GPTT - Demand Calculation
- Fixed Demands -
Equation [Hazen Willams |
Length Accuracy [20 —
Total Simulation Time [30
Wave Speed

Cavitation Head Attribute used for pipes "Wave Speed”

N e ] e
Default Wave Speed 4000





Figure T1-15 – Surge System Data – Exercise T1-Surge
Surge Model Setup - Figure T1-15 shows the [image: image397.png]


 or System Data/Simulation Specifications screen for this surge analysis. To go from the baseline data model to the surge model simply select Surge from the System Type dropdown list (you must have a licensed copy of Pipe2016 : Surge) and enter the appropriate data. For most applications a Default Wave Speed can be used for most or all pipes. For this example 4000 ft/sec. is used based on the pipe material (ductile iron) and this value is acceptable for all the pipes and individual values need not be entered. The value used for wave speed will appear in the Pipe Data as shown in Figure T1-16. Pipe2016 includes a tool to help you calculate the wave speed and the result is close to 4000 ft/sec. The Total Simulation Time will depend on the pipe lengths and must be determined by the user. The Length Accuracy defines the maximum possible difference between model and actual pipe lengths and is typically 10 to 100 feet.

The cause of the transient is a 2-second shutdown of the 1200 gpm flow exiting the dead end.  This type of transient occurs normally as the result of a valve closure. However, it is not necessary to install a valve to analyze the transient. Surge has the capability to model a specified demand change.  This is set up using Change Data as shown in Figure T1-16. When a surge analysis is run using Pipe2016 : Surge a pressure trace is generated as the solution progresses. It is not necessary to set up this plot but it is a useful feature. The setup is shown in Figure T1-16, Node 5 is the dead end (it may be named differently in your model). The limits (Min and Max) should be set by the user based on the anticipated pressure range.

[image: image398.png]Name |5

Pipe Type
Diam|8 ad}
Mirl =

W Spd [4000 ~]

Lengthls75 v F

Rough[i20 W F

Fittings



   [image: image399.png]Name 5
Pie Type  |diameter 6
ave Speed 4000

Cength 675
Roughness 120
Fittings

First Node 4
LastNode 3

JResidential lieters 0

WA
HEEB

install Year





Pipe Data with Wave Speed

[image: image400.png]Node Changes

] o

Time/.
Case

CERERECRES
2 dtm o
4 do

Value




  [image: image401.png]Changes for 5

[rime [change Valie
v demand 1200
B demand 1200




  
Demand Changes

[image: image402.png]


  [image: image403.png]Screen

Plot Data

Use Selected Node

Nade

Min Head

Max Head

Title

3

Inlet

0

j500

forn shutdown




Screen Plot Setup
Figure T1-16 –  Surge Data Screens– Exercise T1-Surge
Results 
The results for the pressure at the dead end node are shown in Figure T1-17. This shows that a maximum pressure of nearly 160 psi occurs due to the flow rejection. It should be noted that this transient is caused by a uniform change in the demand from 1200 gpm to 0 over 2 seconds. A valve closure will produce a transient based on the characteristics of the valve and will be different for each valve and different from the result shown in Figure T1-17.

[image: image404.png]160
140
120

=)
S

80
60
40
20

Pressure

Pressure at Dead End

10

15 20
time (sec.)

25

30




Figure T1-17 –  Surge Analysis Result– Exercise T1-Surge

Using the Pipe2016 : Surge Option for Cavitation Calculations 
The surge analysis is repeated for a more rapid shutdown (0.5 seconds) and the results are shown in Figure T1-17a. The faster shutdown produces a much more severe surge with pressure spikes in excess of 350 psi and extensive cavitation. This response is caused by the fact that the shutdown is completed before sufficient negative wave reflections have time to travel back to the source of the disturbance (dead end).
[image: image405.png]400
350
300

Zas0

© 200

3 150

8
£100

Pressure at Dead End (0.5 second shutdown)

10

15

time (sec.)

20

25

30




Figure T1–17a  Pressure at Dead End – 0.5 second shutdown
The above example illustrates a typical transient calculation for the effects of cavity formation and collapse. Cavity collapse causes pressure spikes which are reflected negatively from reservoirs and other components and cause additional cavity formation and collapse and a severe response as depicted in Figure T1-17a. Transient flow models tend to predict the very worst response for this situation. In reality vapor cavity formation and collapse will release gasses which will soften the response.  Surge provides a technique to model this softening of the effect of cavity collapse and the formation of pressure spikes. To do this the user can enter a number which represents the number of computational time intervals over which the collapse occurs. This data is accessed under [image: image406.png]


 or System Data | Simulation Specifications using the Additional Data/Demand Data button as shown in Figure T1-17b.
For this analysis the transient was calculated using a input of 20 time steps to soften the effects of cavity collapse. The results are shown in Figure T1-17c. This response is much more representative of measured responses where the cavitation tends to die out after several cycles of cavity formation and collapse.
[image: image407.png]



[image: image408.png]Map | Map Settings System Data | Other Data | Setup/Defauts | Report |
Simulation Specs | Other | Reports | Preferences |

System Type [Surge )

Demand Data

Surge System Data

‘Specific Gravity [1
User Units | Units [GPM K
Equation [Hazen Willams =] ‘Optional Stabilization Settings

o CV Setting for Inertial Effects

Time Steps for Cavity Collapse

Length Accuracy [20
Total Simulation Time 30

Cavitation Head

Time Step Increment.





Figure T1– 17b Surge System Data to set Cavity Collapse Time Steps
[image: image409.png]Pressure at Dead End with and w/o Cavitation Collapse Input (20 intervals)

‘l’ N“‘ | Wl " Lt ) | w Lk i “v‘ i ’w

tlme (sec. )




Figure T1–17c  Pressure at Dead End – 0.5 second shutdown with and w/o Cavity Control Data (20 time steps for Cavity Collapse)
2) Surge Analysis - Modulating Regulating Valves – Training Exercise #1
This example exercise shown in Figure T1-18 is used to illustrate several methods which are available to handle regulators for surge analysis. This exercise calculates the transient caused by a 2-second ramp down of the demand at the dead end line from 1200 gpm to 0 gpm.  A PRV set to 30 psi is positioned as shown in the supply pipe. Three options are available for modeling the PRV:

1) The regulator is handled as a constant resistance valve with the resistance based on the initial conditions at the valve (flow and pressure drop) 
2) The regulator is handled as a modulating active valve (AV) with the initial and final settings based on the initial and final conditions for the regulator (flow and pressure drop)
3) A Modulating Regulator is modeled such that the regulator (RV) automatically modulates to hold the setting. The user specifies a time required to modulate by the amount of the initial setting which sets the response time. 
For option 1 and 2  the conditions for the regulator are determined by running the steady state analysis for the initial condition (1200 gpm demand at dead end) and final condition (0 gpm demand at dead end) and looking at the RV report in the tabulated results. These give the following conditions for the PRV:
    VALVE    VALVE    VALVE  SETTING         UPSTREAM  DOWNSTREAM THROUGH

    NAME     TYPE      (psi or gpm)            (psi)      (psi)    (gpm)

 ------------------------------------------------------------------------------

      RV-1    PRV-1    30.00  ACTIVATED       77.67      30.00    2050.51

      RV-1    PRV-1    30.00  ACTIVATED       82.95      30.00     896.21
Based on these results the fixed resistance for the valve can be computed from the initial condition as 5.28. Figure T1-19 shows the pressure transient at the dead end with no modulation of the valve setting.

[image: image410.png]Setup and Run 60 second Surge Analysis

Wave speed = 4000 f/s (ductile)

PRV (30 psi)
3 cases
1) no modulation
2) AV modulation (tool)

3) RV automatic modulation Shutdown 1200 gpm

flow in 2 seconds




Figure T1–18  Training Exercise #1 - PRV set at 30 psi in Supply Line
The second option employs the Modulating Valve Tool as shown in Figure T1-20 to compute the settings for an Active Valve which modulates from the correct initial setting to the correct final setting. The user specifies the time period over which the modulation occurs and Figures T1-21 & 22 show results for 2 and 40 second response times.

The use of the Surge Modulating Valve option is illustrated in Figures T1-23 and 24. Figure T1-24 compares the results with and without modulation of the RV. The response time for modulation is set to 2 seconds. Which means the modulation will occur fairly rapidly.  It can be seen that this approach provides results very similar to option 2.
[image: image411.png]Pressure at Dead No Modulating (PRV-30 psi)
200

160

]
=]

@
=]

Pressure (psi)

N
o ©

o

10 20 30 40 50
time (sec.)




Figure T1–19  Pressure at Dead End – no RV Modulation (constant resist.)
[image: image412.png]Unis

& Engish 81 | C Head & Pressure

Sp.Graviy=[i Flowate [ .

& Wide Dpen Resistance

€ Flow Cosffciert

Inial Steady State Condiions
Upstream Pressure [7757
Downstieam Presswe 33
Flowale [20605

Finsl Steady State Condiions
Upstream Pressure [g755
Downstieam Presswe 33
Flowate G52

psi

Resistance - Headlass / {Flow"2},

where Headlass s in feet or meters
and Flowis in cubic fest per second
or cubic meters per second

Flow Coefficient = Flow (in gpm or
m°3/hr) thet develops a pressure
drop of 1 psi or 1 bar across the valve

Modation Settings

‘Wide-open Resstance /5.0000
Iniia Ratio [§573
FinalRalio [§203





Figure T1–20  RV Modulation Tool to Compute AV Settings
[image: image413.png]Pressure (psi)

200

160

A @ N
S o o

o

Pressure at Dead End - Modulating (2 seconds response)

o

10

20 30 40 50
time (sec.)

60




Figure T1–21  Pressure at Dead End – AV Modulation Tool (2 sec.)
[image: image414.png]200
=160
o 120
80
40

(psi

Pressur

Pressure at Dead End - Modulating (40 seconds response)

10

20

30 40
time (sec.)

50

60




Figure T1–22  Pressure at Dead End – AV Modulation (40 sec.)
[image: image415.png]Name|RV-1

[Regulator

Elevation|90

Regulator Type




[image: image416.png]Device Data

Resp Time|2

 foduating



  [image: image417.png]Regulator
RV
%





Figure T1–23  Menu Boxes for Modulating RV (PRV set at 30 psi)
[image: image418.png]S s N
©® N O O
S o o o

Pressure (psi)

N
S

o

Pressure at Dead End - with & w/o Modulating RV (PRV-30 psi) - 2 second response

o

10 20 30 40 50 60
time (sec.)




Figure T1–24  Pressure at Dead End – RV Automatic Modulation (2 sec.)
Training Exercise #2 – Pump Stations and Pumping Costs (pump design.p2k)
System Description - (Pump Design.P2K) It is necessary to pump 10000 gpm (water) from an elevation of 1000 feet to an elevation of 1900 feet using the arrangement shown in Figure T2-1. This arrangement is based on a requirement for a process used by a major industry. To accomplish this two pump stations are used as shown. Each station has multiple pumps in parallel. In order to control the flow one pump is equipped with a variable frequency drive (VFD) to vary the pump speed. The variation for this single pump is limited to 10% of rated speed. Your task is to determine the number of pumps required for each pump station and the speed required for the VFD pump. Assume that each of the short pipe lengths are 50 feet and all pipe is 16 inch ductile iron (di).  Note that Pipe2016 can model this arrangement using just 2 pump elements in parallel. One element will be for the identical multiple pumps and the second models the VFD pump. Also note that very precise control of the flows is required to maintain the level in the intermediate tank.

Additional analysis (pump design 2.p2k) - 

1) Determine the cost/day for this pumping requirement. There are additional solutions for the pump arrangements. Determine an alternate solution and compare the pumping costs for both solutions. Power cost is $0.08 (8 cents) per KWH

2) Determine if 12000 gpm can be pumped using the available pumps and the same arrangement. If so determine the number of parallel pumps required and the speed for the VFD pump. If you determine that a pump station is not capable of providing this flow make a recommendation that will upgrade the capability and provide the calculations to support your recommendation.

3) Develop System Curves for the two pump stations and plot these with multiple pump curves for the available pumps. This should provide additional insight into the performance of the pump stations.

Setting up the Model –The arrangement for the pump stations is shown in Figure T2-2. It is useful to develop a system curve and plot it with the multiple pump curves for parallel pumps as shown in Figure T2-3. This shows that four fixed speed parallel pumps are not adequate and either 3 identical pumps with the 4th operating at a speed ratio >1.0 or 4 parallel pumps with a 5th operating at a speed < 1.0 will be required. Hydraulically, either of these arrangements will be acceptable as long as the speed required for the VFD pump is within the specified range (.9 – 1.1). The better arrangement will be the one which uses less total power resulting in a lower operating cost.

To evaluate the pumping cost, set up a 24-hour EPS at 1 hour increments and enter the Power Cost ([image: image419.png]


 or System Data/EPS). The report will give the Total Power Cost.

Solutions – One solution (Pump Design.P2K) which meets the specifications is for 3 parallel pumps and the VFD pump operating at a speed ratio of 1.0265 at PS #1 and 6 parallel pumps with the VFD pump operating at 1.057. The power cost for this solution is $6035/day.

[image: image420.png]- elevation = 1800
pressure = 40 psi

all pipe - 16 inch di (C=130)

tank maintains 10 foot head - elevation = 1400 f.

resetvoir maintains
5 feet head
- elevation = 1000 ft.

+ PS#1




[image: image421.png][
54500
505.00
345.00

FLOWRATE
(gpm)
0.00
2000_00
400000

EFFICIENCY
=)
67.00
75.00
65,00




Data for PS#1

[image: image422.png][
s00.00
58000
50000

FLOWRATE
(gpm)
0.00
2000_00
400000

EFFICIENCY
=)
65.00
7300
60.00




Data for PS#2
Figure T2-1 Data for Training Exercise 2

[image: image423.png]


[image: image424.png]Name[Pump4

Pump -

Elevation| 1000

Sp Ratio|

mp Type——
 Table C File
 Const(™ Rated

| e ]|




[image: image425.png]PumpType
 Table C File
 Const(™ Rated

N





[image: image426.png]Node Type  Pump - Table

ame. Pump4
Elevation 1000

itle
Parallel 5 Parallel
D 1
ICheck Valve X
hion-Reopening Che
IBypass Line
oV Time 0

ICV Resistance 0
I5ypass Resistance )

ISpeed Ratio 1



[image: image427.png]I5ypass Resistance )

ISpeed Ratio 1035

TS





Figure T2-2 Pump Station Model for Training Exercise 2
[image: image428.png]8000 10E+4  12Ev4  14E+4  16E4
FLOW





Figure T2-3 Pump Station #1 System Curve and Multiple Pump Curves

Training Exercise #3 – Hydraulic Analysis of Sprinkler System
System Description (Demo Fire Sprinkers.P2K) - A sprinkler system layout is shown in Figure T3-1 (plan view). Water is supplied by a connection to a city water main. A fire flow test at a nearby hydrant gives the data shown to characterize the supply to the sprinkler system. The sprinklers are ½ inch orifices and are fed through a 1 foot long 1 inch nipple (vertical with the ½ inch orifice exit 1 foot below connection). A 20 foot grid is provided to determine lengths. The connecting pipe (from the supply) rises 30 feet vertically to the sprinkler system (this length must be added to the total length).  Set up an analysis with all 4 sprinklers operating. Assume all pipe has ID = 2.0 inches with a HW coefficient = 120. 

Additional analysis - The minimum flow required through any sprinkler is 35 gpm. If this requirement is not met carry out additional analyses with a larger connection to the supply.

[image: image429.png]all pipe = 2 inches
HW Coefficient = 120 T
—_— @

1/2 inch orifice

hose demand =100 gpm --- --- elevation = 30 ft.

2 elbows - Angle Valve

--elevation = 0 ft.

static pressure = 100 psi
residual pressure = 50 psi @ 500 gpm




Figure T3-1 Data for Training Exercise 3

[image: image430.png]. Pipe2000 - Sprinkler/Blowoff C.
Unit [Engish -

Compude Based on [SuggentedVakes <]
Orifice Size (in)  Ks

[ —

[Ke=0/(@ 0] where Ks f spikler corstant,
[0 fowate in gpm {or /5] and dP i pressure
o i psi or kPa)





Sprinkler Constant Tool

[image: image431.png]Name|s6
SprinklerfLeak <

Elevation 30

r——
Constant |56
—

Length

—

Diameter|!
T

Elev Chal!
G
Elbows

CR—




[image: image432.png]Node Type  Sprinkler/Leak

Name 6
Elevation 30

itle
on/oft Ev4
Constant 56
Length 1
Diameter 1

Elevaton Change 1

Elbows 0




Sprinkler Data

[image: image433.png]Name[ps1—
Pressure Supply =

Elevation 0
S

Gage Difl0
nelit___

Static Pr|100
static]

Res Pr/30

Res Flow/500
—_

W Rated

Main Supply



[image: image434.png]Node Type  Rated Pressure Sup

IName =]
Elevation 0
itle

fon/oft Ev4

gnore Changes

(Gage Diference 0

IStatic Pressure (100
JResidual Pressure 50
Residual Flow 500
IMain Supply X




Pressure Supply Data

Figure T3-2 Sprinkler and Pressure Supply Data for Training Exercise 3
Setting up the Model – Pipe2016 includes a tool for determining the sprinkler constant based on the orifice size. The use of this tool is illustrated in Figure T3-2 along with the setup screens for the sprinkler and pressure supply. Note that the data for the 1 foot long nipple is included with the sprinkler and the elevation change is entered with a (–) sign because the sprinkler nozzle is 1 foot below the piping system. 

The hydraulic analysis of a sprinkler system often includes the requirement to provide for a fire hose demand at the supply or at some interior node (or both). For this exercise a hose requirement of 100 gpm is specified at the node where the riser pipe connects into the sprinkler system. This requirement is accommodated by specifying a demand of 100 gpm at that node. Note that the pipe from the supply to this node includes an additional 30 foot riser and there are several fittings in this line which should be modeled. Two additional T connections which should be included in the hydraulic analysis are noted. 

Analysis Results - Figure T3-3 shows the pipe and sprinkler flows for the hydraulic analysis using the baseline data. This shows that the 35 gpm requirement is not being met. Two additional simulations are set up using a 3-inch and a 4-inch connection. This is done by providing Change Data for this pipe as shown in Figure T3-4. The Change Type is selected as Diameter and 2 additional simulations are set up. Figure T3-5 shows the pipe and sprinkler flows for a 3-inch diameter connection and this provides the required 35 gpm flow.

[image: image435.png]53.7

108.2

100

53.7

545

26.9 253

27.3 270

26.8

27.2




Figure T3-3 Pipe and Sprinkler Flows (2 inch connection) for Training Exercise 3

[image: image436.png]Roughness
Minor Loss

Pipe Open

Pipe Closed

Delete This Change



[image: image437.png]Pipe Changes

o]

Time/.
Case

Value




[image: image438.png]Valie





Figure T3-4 Changes to Increase Connecting Pipe Size for Training Exercise 3
[image: image439.png]141

100

704 351 35 35

I 35.5 354 35.4




Figure T3-5 Pipe and Sprinkler Flows (3 inch connection) for Training Exercise 3
Section 4 - Case Studies
Case Study #1 - Landfill Gas Extraction Piping System (Landfill Gas Extraction.P2K)
Description – Pipe2016 : Gas provides an excellent modeling tool for designing and analyzing a landfill gas extraction system. There are several approaches to modeling the extraction system and a simple yet accurate modeling approach is illustrated below in Figure CS1-1. A compressor (fan – blower) at the collection point provides a vacuum on the piping system. The vacuum is usually on the order of a negative 15 – 30 inches of water (around 1 psi or less). This vacuum must be sufficient to provide a vacuum at each collection point sufficient to pull in the required amount of gas. For this example it is assumed that each of the collection nodes will collect 60 SCFM (standard cubic feet/minute) of gas. Thirteen collection nodes are modeled at the end of 4-inch pvc pipes (light). The rest of the collection system is 8-inch pvc (dark).

A control valve will be positioned at the well head collection nodes. The piping system and compressor must be sized so a sufficient vacuum is pulled at each of the collection points. The required analysis is easily done by designating the desired inflow at each well head and calculating the vacuum pressure required. If this pressure is sufficient to allow the control valve to be set to a proper setting to set the flow using the available pressure drop then the collection system will work. If this is not the case either larger pipes or a larger compressor will be required. Conversely if the pressure differences are significantly larger than required then smaller pipes or a smaller compressor may be used.
Model Data – The Gas System Data screen is shown in Figure CS1-2.  For this example methane properties are used. However, landfill gas will not be pure methane so the gas properties for the extracted gas should be used. The Gas model provides a Lookup Properties tool which will give the necessary properties for methane at 86 degrees F. as shown in Figure CS1-2 (specific gravity, viscosity etc). Note the flow units of SCF/min and pressure units of inches of water are used. These units are commonly used for landfill gas extraction studies.
[image: image440.jpg]1000 feet

N

Methane
Temp. =86 F
Viscosity = 2.33E-7

60 SCM Into each
[~ collection node

o

Landfiii Gas Extraction system

"





Figure CS1-1  Landfill Gas Extraction System
KYnetic System Data icon:  [image: image441.png]



[image: image442.png]Map | Map Settings System Data | Other Data | Setup/Defaults | Report |
Simulation Specs |Other | EPS | Reparts | Preferences | Skeletonize/Subset

Gas System Data

Sl Units [~ Flow Units

[scFimin  ~]

Pressure Units

Operating Temp
‘Specific Gravity

Ratio of Specific Heats.
Absolute Viscosity

Gas Density
Molecular Wt
Critical Temp.

Critical Pres

inches water (g ]
/86
5545
131
[233E07
I Use
¥ Use

I~ Use

System Type |(;as -
Lookup Properties
Demand Pattern =
Patter Name Clear Patter |
[none
Select Pattem

Change Pattern

Patter Name Clear Patter |

Select Pattemn





[image: image443.png]Properties of Gases (CopyRight KYPIPE LLC 2012)

© Acetiens  Ettylere € Nitogen & EngishUnits 5l Unis
A £ Ethyl Chioide © Nirous Dsice Temperatue= G5 F
® R © Helum @ S B |
© Aigon  Hydrogen C Pentene. Rato of specfic heats = [137
€ Benzene  Hydogen Cyaride " Propane Absolte Viscosiy = [LO0000023338 i p
 Butane C Hydiogen Sulfide C Propyens. 2333507
C CabonDisie € Kupton € SulturDioside: CiealTenperatue = [342.72 Farkine
C CabonMonoide & Methane  WeterVapor il ETRE
 Chitne © MetryiChoide " Xenon Moleulr Weiht = [i6 04
© Ethane © Nt Oide

Disclainer Ext





Figure CS1-2  System Data for Landfill Gas (methane)
[image: image444.png]40|
100
30] 80|
[
80|
80| (70|
700
1
80
700 80)
80| 80|
\ i
700 }.,,J
LR
1
L'FA





Figure CS1-3  Elevation Data for Landfill Gas (methane)
[image: image445.png]


[image: image446.png]



Pipe Data

[image: image447.png]


[image: image448.png]



Compressor Data

[image: image449.png]


[image: image450.png]lode Type _ Junction Single Der

Elevation 100




Junction Data

Figure CS1-4  Pipe, Reservoir and Junction Data
The pipes are all pvc and a roughness of 0.1 millifeet was used as illustrated in Figure CS1-4. Node elevations are noted in Figure CS1-3. Because the analysis is for gas the elevations will have a very small effect on the results. However, elevation data may be entered for each node. The reservoir represents the suction pressure for the compressor and should be set to the desired value. For this example we used -15 inches of water. This implies that a compressor is required which produces 15 inches of water pressure at a flow of 780 SCFM. The junction data includes a negative demand of 60 SCFM to simulate the amount of gas extracted from each well head.

Results – The pressures and flows for the Pipe2016 : Gas simulation are shown in Figure CS1-5. The analysis shows that the pressure drop across the control valve at the well heads vary from 6.7 to 4.9 inches of water (assuming the well head pressure is atmospheric). This should be sufficient to overcome losses through the control valves and control the flows. Required valve settings can also be determined. For example, the valve setting for the smallest pressure differential (4.9 inches) means that the control valve will be set such that 60 SCFM will cause a pressure drop of 4.9 inches of water. This data allows the selection of an appropriate valve. It should be noted that identical results will be obtained if the reservoir representing the compressor suction is replaced by a compressor (pump) which operates at 15 inches and 780 SCFM while discharging the gas at atmospheric pressure.
[image: image451.png]Vﬁﬂ ﬂ
Vm%
3 B
S
B b ‘N-/N o 4
én. 5“\ Ua\.
3 5/
1F 5 ES
BE 2 “.,.\
&> Mw V\s !
v
N
™
\

s





Figure CS1-5  Pressures (inches of water) and Flows (SCFM) in Collection System
A further illustration of the power of modeling for design is shown in Figure CS1-6. For this analysis the pipes highlighted were closed (essentially removed from the collection system). The resulting pressures and flows are shown. The results show that removing the upper pipe lowers the vacuum pressures 30% or so. Removing the lower pipe results in an unacceptable design (vacuum is not attained at some collection nodes).

[image: image452.png]4.1
/4.4
2

-7.2

-7.2

},{d





[image: image453.png]i
X
2
< i
3 ._ s, o
] o
P! p S,
5 AR
S8 .,g.\ !
B 28 ¥ “
A& . n“
R
i
L
N
\
\
A

LB





Figure CS1-6  Pressures and Flows (SCFM)  - no Loop
Case Study #2   Modeling Air/vacuum Valves with Surge (Air Vacuum Valves.P2K)
Figure CS2-1 shows a simple Surge model which simulates a pump trip and evaluates the effect of 2 air/vacuum valves. The pump station delivers 350 gpm @ 100 feet of head and is modeled using a Pump Junction Node. A pump trip is modeled by ramping the flow from 350 gpm down to 0 in 4 seconds. Figure CS2-2 shows the pressures at 2 locations when there is no surge protection (air/vacuum valves are closed). 

[image: image454.png]1092 ft.

8 inch di - HWC = 130, C = 3900 ft/sec

Discharge Reservoir (1097 feet)

Pump Station (1010 feet)
350 gpm @ 100 ft.





Figure CS2-1  Surge Model with Air/vacuum Valves
[image: image455.png]Pressure at PS & High Point (1092 ft.) w/o Surge Protection

20 30 40 50
time (sec.)

60




Figure CS2-2  Pipe2016 : Surge Model Results - no Air/vacuum Valves

Figure CS2-3 shows data for three different setups for the 2 air/vacuum valves. For the first the outflow orifice is much smaller than the inflow orifice. This design is intended to allow a lower controlled release of air and prevent “air slam”. The results for the PS and high point are shown in Figure CS2-4 and very small pressure spikes occur when the air is all expelled.

It is possible that an air valve could experience a short delay before air enters the pipeline. For rapid pressure drops (pump trip) this could allow pressures significant lower than atmospheric pressure to develop prior to activation. Pipe2016: Surge allows the user to specify a delay as shown in Figure CS-2b. The results obtained with a delay for one air valve (but not the other) are shown in Figure CS-5.

A third set of results were obtained using the same 2 inch orifice for inflow and outflow. The results for this analysis are shown in Figure CS-6. As shown significant pressure spikes occur as the result of “air slam”.

[image: image456.png]Device Data
Inflow D[2
Outflow D025

Init Vol [0




 [image: image457.png]172 Stage Afr Vacul
3
052





2-Stage

         [image: image458.png]Inflow D)

Outflow D|
Init Vol




  [image: image459.png]12 Stage Air Vacu

IName oy
Elevation 1092





With a Delay

  [image: image460.png]Device Data
Inflow D[2

Outflow D[2
Init Vol [0




[image: image461.png]ame
Elevation 1092

Title

On/oft o
el Gas Volume 0

inflow Diameter 2

Outfow Diameter2

Delay 0

Disc Coef 0




Single Stage
Figure CS2-3  Surge AV Data Screens

[image: image462.png]Head (ft)

160
140
120
100

Pressure at PS & High Point (1092 ft.) with 2 stage air valves for Surge Protection

S USSRy B (W 1!

0 20 40 60 80 100 120

time (sec.)




Figure CS2-4  Surge Model Results – 2 Stage Air/vacuum Valves

[image: image463.png]Pressure at air valves with 2 stage air valves and 1 second delay for AV#1

0 20 40 60 80 100 120
time (sec.)




Figure CS2-5  Surge Model Results –2 Stage Air/vacuum Valves - 1 sec. delay
[image: image464.png]300
250
200

€150

©
£100

Pressure at air valves with single stage (2 inch) air valves - no delay

L

I

20

40

60

time (sec.)

80

100

120




Figure CS2-6  Surge Model Results – Single Stage Air/vacuum Valves

Campus Pipe Distribution Facilities Modeling
Pipe2016 has unique capabilities to model facilities piping systems. This provides a powerful modeling platform for all the various distribution systems which may be part of a campus or industrial facility physical plant. The following distribution system types can be modeled and analyzed using Pipe2016.

1) potable water distribution system including fire hydrants

2) chilled water supply and return systems

3) hot water distribution systems

4) gas distribution systems (natural gas, air or any gas)

5) saturated or superheated steam distribution systems

All of the Pipe2016 series models employ the same easy-to-use graphical user interface (GUI) which means that once a user becomes familiar with the GUI they can utilize the full range of the Pipe2016 capabilities and models. The user merely selects the appropriate module from the Pipe2016 [image: image465.png]


 or System Data | Simulation Specs menu.

[image: image466.png]System Type |Steam -





Figure CF-1 Pipe2016 Module Selection
KYPipe and GoFlow use the powerful KYPipe engine (as well as Surge for steady state) which analyzes all kinds of liquid distribution systems. The Steam model is used for saturated and superheated steam distribution and the Gas model handles all gas distribution systems. In addition a transient liquid flow model (Surge) is available to do pressure surge analysis on any liquid flow system. This adds an extremely important capability to this comprehensive package of distribution system modeling software.

The following simple modeling examples are presented in this section to illustrate modeling of Campus distribution systems. The data file names are noted.

      1)   Potable Water Distribution & Fire Flows (Campus Potable Water.P2K)
2)   Chilled Water – supply & return (Campus Chilled Water.P2K)
3)   Hot Water Distribution (HotWater.P2K)
4)   Gas Distribution (Campus Gas Distribution.P2K)
5)   Saturated Steam Distribution (Campus Steam Distribution.P2K)
6)   Superheated Steam Distribution (Campus Superheated Steam.P2K)
A scaled map of a small but typical campus is shown in Figure 2. This is used as a background map for the following Campus Facilities distribution system examples.
[image: image467.png]



Figure CF-2  Scaled Campus Map
1)  Potable Water Distribution Model (Campus Potable Water.P2K)
Figure CF-3 shows the layout of a potable water system. This system is fed from a water main in the city distribution system which has the characteristics shown based on a fire hydrant test of a nearby fire hydrant. Figure CF- 4 provides additional data on pipe sizes, roughness and demands. The data file for this example is Campus Potable Water.P2K (Examples button – 6 Campus Facilities folder).  For the sake of simplicity all elevations are set at 400 feet. Demands of 75 gpm are located at each building as shown in Figure CF-4 (large nodes) The supply is accurately modeled in Pipe2016 using a Variable Pressure Supply as shown in Figure CF-4. This device accounts for the pressure drop at the supply based on the amount of flow going to the campus. Data boxes for nodes and pipes are also shown in Figure CF-4

Five fire hydrants are located as shown. The following simulations were carried out: 
1) Average Demands for Each Building (75 gpm)
2) Peak Demands for Each Building (GDF=1.4)

3) Fire Flow at Average Demands and Peak Demands

[image: image468.png]connection to
distribution syste
i static, 2000 gpm @ 75 psi





Figure CF-3 Potable Water System With Scaled Campus Map
Campus Facilities Example 1- Results

1) Average Demands for Each Building (75 gpm)

Figure CF-5 shows pressures at the buildings for this analysis.

2) Peak Demands for Each Building (GDF=1.4)
The demands at each building were increased to 105 gpm (75*1.4). Figure CF-6 shows pressures at the buildings for this analysis.
3) Fire Flow at Average and Peak Demands
The fire flow which can be delivered at each hydrant while maintaining 20 psi at all locations in the piping system is determined by selecting the Pipe2016 Fireflow Calculations option shown below. The Pipe2016 Fireflow report is also shown. Figures CF-7 & CF-8 show the available fireflows for these cases.

[image: image469.png]Fireflow with specified min pressure Minimum Pressure for Fireflows [20

Static Pressure Limit [20 (nodes with static pressure below this value will be ignored)
Fireflow Nodes
 Selected Hydrants
@ Al Hydrants
€ Selected Junctions Nodes
€ Al Juncion Nodes W Clear Old Results

I™ Generate Flushing Report (Hydrants and Blowofs)




[image: image470.png]Byarant Elevation Demand Static Flow-1  Flow-2  Node-2

Node. gem Pressure gem e
4 200.0 0.0 5.6 5313 745.9 525
B5 400.0 0.0 75.0 1418.1 11348 J-25
Bl 400.0 0.0 60.3 456.0
B3 400.0 0.0 62.2 660.5 631.1 J-25
B2 400.0 0.0 61.1 553.2 540.7 J-25




[image: image471.png]8 inch PVC|

HW C value = 140- all pif

demand = 75 gpr

[4 inch PVC]|

6 ich PVC|





[image: image472.png]


[image: image473.png]Name VP

Elevation 400
Title

On/oft Ev4
ignore Changes

Gage Difference 0

Static Pressure 90

Residual Pressure 75

Residual Flow 2000




Rated Pressure Supply Data

[image: image474.png]


[image: image475.png]Junction Single Der





Junction Data

[image: image476.png]


[image: image477.png]LLLLLLLLLL
LLLLLLLLLL
rr P

em

3583;



[image: image478.png]



Pipe and Fittings Data
Figure CF-4  Data for Potable Water System Model
[image: image479.png]



Figure CF-5  Pressures @ Average Flow (1125 gpm)
[image: image480.png]



Figure CF-6  Pressures @ Peak Flow (GDF-1.4)
[image: image481.png]......

I:-_ 0

i
ey |





Figure CF-7  Fire Flow @ 20 psi Minimum (average)
[image: image482.png]......

W

i
Sl





Figure CF-8  Fire Flow @ 20 psi Minimum (peak)
2)  Chilled Water Model (Campus Chilled Water.P2K)
A Pipe2016 Model for a Chilled Water Supply and Return system is shown in Figure CF-9. The system consists of the higher pressure supply piping and lower pressure return piping as shown. All main pipes are 6-inch and pipes to and from buildings are 4-inch. Flows to buildings are controlled using flow control valves as shown. Additional modeling details are shown below. Loads of 100 and 80 gpm for each building were analyzed. The data file for this example is Campus Chilled Water.P2K (Examples button – 6 Campus Facilities folder).Typical results are shown in Figure CF-10
[image: image483.png]



                        [image: image484.png]Flow Regulators
simulate valves
which control the
flows to buildings

[ S

/

Supply side Hydraulics
determines the pressure
available at the building

If supply side pressure

at the flow control valve

is not sufficient the flow

control valve will open wide
land provide less flow which

‘ can be accommodated by

the return side

Return side Hydraulics
determines the pressure
required at the building
to transport water back

to pump & chillers 31




         
Figure CF-9   Chilled Water Model
[image: image485.png]Results — Peak and Average Loads

REGULATING

VALVE
LasEL

VALVE
TYPE

VALVE REPORT
VALVE  VALVE
SETTING  STATUS  PRESSURE
(pss or gpm) (p22)

UPSTREAM DOWNSTREAM THROUGH
PRESSURE FLOW
)

(gpm)

Peak Load

100.00 ACTIVATED | 33.31 947 100.00
100i00 ACTIVATED  15.96 1471 100.00

100l00 ACTIVATED 5939 olss 100,00

100l00 ACTIVATED  2s.e9 eiss 100,00

100100 ACTIVATED  20.69 7.1 100,00

100l00 ACTIVATED  1s.65  10.57  100.00

100l00 ACTIVATED  17.79  12.56 10000

Unable to 00.00 ACTIVATED  15.65 15.53  100.00
100.00 WidE OFEN  1s.56  is.s6  sd.s1

maintain load 100l00 WIDE OPEN  15.55  1s.59  s.67
RV-1  FCV-1  80.00 ACTIVATED  ds.6e 650 s0.00

RV-10  FCV-1 00,00 ACTIVATED  35.11  11.50  £0.00

Rv-2  FCv-i  80.00 ACTIVATED  €8.12 026 000

RV-s  FCV-1  80.00 ACTIVATED  45.32 ese 000

RV-4  FCV-1  £0.00 ACTIVATED  39.01 s.e7 000

RV-s  FCv-1  80.00 ACTIVATED  37.37 21 sol00

RV-6  FCV-1  80.00 ACTIVATED  36.67 a1 000

RV-7  ECV-1 80,00 ACTIVATED 3477 1225 €0.00

RV-s  FCV-1  80.00 ACTIVATED 3454 12.46 0.0

mves  reves  20.00 AcTTVATED a4 .44 is.e1 2s.00

Average Load



    

[image: image486.png]e

A ?h‘ﬂ "
iy l= N





Figure CF-10   Chilled Water Model Results
3)  Hot Water Model  (HotWater.P2K)
A Pipe2016 Model for a Hot Water Distribution System is shown in Figure CF-11. The main feature of this distribution system is that the water is superheated. Significant temperature changes occur as the flow is distributed from the boiler to the buildings. This causes significant changes in the density and the viscosity of the water.  It is necessary to provide a temperature vs. density & viscosity table for the superheated water. This is done using a Pipe2016 Tool as shown in Figure CF-12. It is also necessary to employ the Darcy Weisbach head loss formula because of the variation in the properties of the hot water. Input data for the supply (boiler) and all nodes are provided as input data. These values are shown in Figure CF-13. The data file for this example is HotWater.P2K (Examples button – 6 Campus Facilities folder).
The model was analyzed for a range of building loads (8 – 14.8 gpm). Pressures at the buildings are shown in Figure CF-14 for the low and high loads. Figure CF-15 shows the pressure variations at several buildings. Figure CF-16 shows the tabulated results which include the density and viscosity variations.
[image: image487.png]Supply: 450 F
@ 200 psi

Roughness = 0.3 millifeet
Average Building Load = 8 gpm

[ 500 feet —]





Figure CF-11   Hot Water Distribution System Model
[image: image488.png]Temperature Vs. Densit Viscosity

Temperatue] Densiy _[Viscosty
Unit [F /3 |r2/sec

| 0 w24 0000166
| ] 624 00000122
3 o 822 0000015
| 100 &2 0.0000142]
| 150 &0 00000046
| 2m % 000000341
— am 0 000002
| 4 ) 0000001

E

i





Hot Water File

[image: image489.png]


 [image: image490.png]



Reservoir Data

[image: image491.png]


[image: image492.png]emperature 450





Reservoir Temperature User Data
Figure CF-12   Hot Water Properties File and Supply Data
                        [image: image493.png]



Figure CF-13   Hot Water Temperatures @ Buildings
[image: image494.png]



[image: image495.png]



Figure CF-14  Pressures – Load = 8 gpm (upper) & 14.8 gpm (lower)
[image: image496.png]Pressures at Selected Buildings

Case




Figure CF-15   Pressures at Selected Buildings

[image: image497.png]PIeE NODE NUMBERS FLOWRATE ~ HEAD MINOR LINE KL/  Kine. Ave Pressure Mass  Ave.
NAME # #2 LOoSS  LOSS VELO. 1000 Viscos. Density  Drop  Flow  Temp
 gem)  (ft) (ft)  (ft/s) (ft/ft) (fth2/s) ( psi) ( 1p/s)

P-1 R-1 J-2 193.21  24.98 0.00 4.93 24.25 0.0000122 52.450  9.098 22.577 412.5
P-10 J-10 g1 44.20 1.22 0.00 2.01  5.55 0.0000031 53.750  0.456  5.293  225.0
P11 g1 J-12 28.80 0.42  0.00 1.31  2.45 0.0000034 55.000  0.159  3.529  200.0
P-12 J-12 723 28.80 0.37 0.00 1.31  2.450.0000034 55.000  0.140  3.529  200.0
P-13 J-2 J-1a 14.40 0.82 0.00 1.47  4.82 0.0000012 42.500  0.242  1.363 375.0
P-1a 15 717 182.80 5.55 0.00 4.67 19.83 0.0000015 45.000  1.735 18.326  350.0
P-15 715 I-16 14.40 0.63 0.00 1.47  4.86 0.0000015 45.000  0.197  1.448 350.0
P-16 717 -5 154.00 5.08 0.00 3.95 14.12 0.0000015 45.000  1.589 15.439  350.0
P-17 717 J-18 14.40 0.44 0.00 1.47  4.86 0.0000015 45.000  0.137  1.448 350.0
P-18 -6 719 14.40 0.65 0.00 1.47  4.53 0.0000020 50.000  0.240  1.608  300.0
P-15 71 J-20 14.40 0.44  0.00 1.47  4.53 0.0000020 50.000  0.154  1.604  300.0
P2 J-2 I3 224.05  18.36 0.00 5.72 29.61 0.0000012 42.500  5.418 21.214  375.0
P-20 I8 J-21 14.40 0.55 0.00 1.47  5.03 0.0000027 52.500  0.202  1.684  250.0
P21 g1 J-22 14.40 0.67 ©0.00 1.47  5.12 0.0000034 55.000  0.254  1.764  200.0
P22 723 713 14.40 0.13 0.00 0.65  0.66 0.0000034 55.000  0.048  1.764 200.0
p-23 723 J-24 14.40 0.46 0.00 1.47  5.12 0.0000034 55.000  0.176  1.764 200.0
P24 713 J-25 14.40 0.03 0.00 0.37  0.16 0.0000034 55.000  0.010  1.764 200.0
P-25 J-a J-1 14.40 1.26 0.00 1.47  4.86 0.0000015 45.000  0.395  1.448  350.0
P-26 717 726 14.40 0.13 0.00 0.65 0.6l 0.0000015 45.000  0.040  1.448 350.0
p-27 -5 727 14.40 1.07 0.00 1.47  4.86 0.0000015 45.000  0.334  1.448 350.0
p-28 -1 728 34.20 0.75 0.00 1.55  3.29 0.0000020 50.000  0.274  3.810  300.0
P25 728 729 14.40 1.78  0.00 1.47  4.53 0.0000020 50.000  0.616  1.604  300.0
P-3 I3 J-a 217.65  15.11 0.00 5.56 27.99 0.0000014 43.750  4.592 21.214  362.5
P-30 728 J-30 14.40 1.38  0.00 1.47  4.53 0.0000020 50.000  0.479  1.604  300.0
P-a -4 J-15 197.20 2.77 0.00 5.03 23.05 0.0000015 45.000  0.864 15.770  350.0
P-5 -5 -6 132.25 3.04 0.00 3.38 10.49 0.0000018 47.500  1.004 13.995 325.0
= -6 77 111.24 1.80 0.00 2.84  7.49 0.0000020 50.000  0.624 12.391  300.0
P71 77 I8 61.11 0.30 0.00 1.56  2.38 0.0000024 51.250  0.108  6.978 275.0
P8 I8 -9 45.26 1.27 0.00 2.05  5.77 0.0000027 52.500  0.463  5.293  250.0
B3 -9 J-10 45.26 1.15 0.00 2.05  5.77 0.0000027 52.500  0.420  5.293  250.0




Figure CF-16   Hot Water Model – Tabulated Results

4) Natural Gas (methane) Distribution (Campus Gas Distribution.P2K)
Figure CF-17 shows the layout of a campus Natural Gas (methane) Distribution Model. This system is supplied from a gas main in the city gas distribution system at 120 psi. Pressure regulators are used to reduce the pressures to the levels desired. The arrangement of the pressure regulators is shown in Figure CF-18 along with additional modeling data. Figure CF-17 provides additional data on pipe sizes, roughness and demands. Properties for the gas are input with the System Data as shown in Figure CF-18.  Pipe2016 provides a gas properties Look–Up Tool as shown. The data file for this example is Campus Gas Distribution.P2K (Examples button – 6 Campus Facilities folder).  For the sake of simplicity all elevations are set at 400 feet. Demands of 300 MSCF/day are located at each building. 

Results of the compressible flow analysis are shown in Figures CF-19 (building pressures) and CF-20 (tabulated results).

[image: image498.png]2 inch pipe
4 inch pipe

Scotand

Roughness = 0.02 millifeet
Average Building Load
= 300 MSCFlday





Figure CF-17   Gas Distribution Model 

[image: image499.png]Load to Building
(300 MSCF/day)

Pressure Regulato[)
Setting = 40 psi

°

Pressure Regulator
Setting = 30 psi

Connection to Gas Main
Pressure Supply
@ 120 psi





[image: image500.png]Properties of Gases (CopyRight KYPIPE LLC 2012)

" Acetylene " Ethylene. " Miogen & English Units 51 Units
C b € Ethyl Chinide © Nitous Oside. Temperatwe= [;5  F
 hnmoria £ Heium © Ogen o Grviyelive o)< [T5575
© Argon £ Hycrogen £ Pentane. Rlio of specifc heats = [137
" Benzene  Hydriogen Cyanide (" Propane Absolute Viscosity = | 200000022525 ¢ v
" Butane " Hydrogen Sulfide " Propylene 2292527
" Carbon Dicxide:  Kiypton  Sulfur Dicxide. Crical Tempsiatue = [34272 GE2ts
" Carbon Monaside: & Methane " Water Vapor Crical Pressurs = [657.1735 (==
" Chiorine " Methyl Chloride: " Xenon Melecularweiht = [16.04
 Ethane " Nitiic Oxide.
E i




 
Gas Properities

[image: image501.png]SlUnits [~ Flow Units [MSCF/day  ~]
Pressure Units [psi (abs)

Operating Temp |75
‘Specific Gravity | 5545
Ratio of Specific Heats |1-31

Gas Density ™ Use
Molecular Wt I Use
Crical Temp. [ -,
Cical Pres.





Figure CF-18   Additional Gas Distribution Model Details

[image: image502.png]



Figure CF-19   Gas Distribution Model Results – Building Pressures

[image: image503.png]pIEE
¥o.

B-1
P-10
P-11
P-12
B-13
P-1e
B-15
B-16
P-17
=
Po1o

NoDE
1

18
3-10
g-11
J-12
&V-2
715
715
317
317

T

RESULTS FOR THIS SIMULATION FOLLOW

NoDE
2

I-2
g-11
g-12
723
3-10
317
I-16

12
I-19
T-20

(o

300.
500,
600,
600,
500,

-600.
300.

-1500.
600,
300.
200,

FLow
55U)

000
000
000
000
000
000
000
000
000
000
900

1085 VELOCITY
(F1/5)

(useU)

2.09
.35
.13
.11
17
.20
78

2.0¢
72
e

EER
1.
a1,
a1,
0.
57,
76.
s2.

156,
70.
e

22
02
00
17
50
7e
&
35
a1
12
a0

DENSITY FRICTION AREA
(#/CF) FACTOR RATIO

o1
Los3
Loz
Loz
Lose
Loss
Loss
.01
Los6
.06
Cio1

L0173
L0157
L0163
L0163
L0157
L0162
L0173
L0125
L0156
L0173
o173





[image: image504.png]JUNCTION

NoDE

TITIE

DEMAND

(uszFw)

300.00
.00
.00
.00
.00
.00

300.00
.00

300.00

300.00

PRESSURE

(useU)

29.
29,
29,
29,
22,
51,
51,
s2.
29.
34.

se
&5
o
3¢
02
2
o0s
o1
E
05

PRESSURE

(ps1)

29.
29,
29,
29,
22,
51,
51,
s2.
29.
34.

se
&5
o
3¢
02
2
o0s
o1
E
05

PRESSURE

(ps16)

1a.
1s.
1a.
1a.
1.
17,
6.
17.
1s.
19.

e
15
7
&
33
12
S
52
2
35

DENSITY

#/cF

o83
Lose
Los3
Loz
078
Loss
087
.0s0
Lose
095





Figure CF-20   Gas Distribution Model – Tabulated Results

5)  Saturated Steam Distribution System (Campus Steam Distribution.P2K)
Figure CF-21 shows the layout of a campus Saturated Steam Distribution Model. This system is supplied from a Steam Plant at 120 psi.  Figure CF-21 provides additional data on pipe sizes, roughness, and demands. The data file for this example is Campus Steam Distribution.P2K (Examples button – 6 Campus Facilities folder).. For the sake of simplicity all elevations are set at 400 feet. Baseline demands of 400 #/hr are located at each building. Analysis highlights include:

Saturated Steam Analysis:
     1) plant provides saturated steam @ 100 psi

     2) saturated steam is distributed to all buildings 
     3) properties of the saturated steam are determined using Steam Tables
     4) Load increases from low (400 #/hr) to high (800 #/hr) 

The model was analyzed for range of building loads (400 – 800 #/hr). Pressures at the buildings are shown in Figure CF-22 for the low and high loads. Figure CF-23 shows the pressures variations at several buildings for the range of loads (400 – 800 #/hr). This shows that the higher loads will not be feasible for all buildings because of low pressures.
[image: image505.png]Steam Plant





Figure CF-21   Saturated Steam Distribution Model 

[image: image506.png]



Load = 400 #/hr

[image: image507.png]



Load = 720 #/hr

Figure CF-22   Steam Distribution Model Results – Building Pressures

[image: image508.png]



[image: image509.png]% Pressures at Selected Buildings

80
70

@
250
°
540
32
830
& 20
10

-10

-1 0 1 2 3
Case




Figure CF-23  Pressures at Selected Buildings – load varies from 400 (case 0) to

800 #/hr (case 5)
6)  Superheated Steam Distribution Model (Campus Superheated Steam.P2K)
Figure CF-21 also shows the layout of a campus Superheated Steam Distribution Model identical to the saturated steam model except for the steam properties. This system is supplied with superheated steam from a Steam Plant at 100 psi and 450 degrees F.  Figure CF-21 also provides additional data on pipe sizes, roughness and demands. Additional details are provided in Figure CF–24. A feature of this model is that the heat loss and resulting temperature is calculated. A heat loss coefficient for each pipe (or a global value) along with the temperature at the steam plant is provided as input data. The data file for this example is Campus Superheated Steam.P2K (Examples button – 6 Campus Facilities folder).. Baseline demands of 400 #/hr are located at each building. Analysis highlights include:
Superheated Steam Analysis
     1) plant provides superheated steam @ 100 psi and 450 degrees F

     2) heat loss calculated using heat transfer  coefficient = 0.15

     3) select “Temperature  Sensitive Analysis” to utilize “superheated steam”
     4) properties of the superheated steam are determined using Steam Tables

[image: image510.png]fName A

PieType ~ PVC-4
Length
Roughness 001

Fittings

FistNode R
LastNode U2
et Transfer Coet0 15,

fnstall Year 2007

frile





KYnetic Heat Transfer Coefficient – User Data

[image: image511.png]Analysis Type

tame [P-1 Other Data

Node 1
= € Reguler
=
[ node2
pvc | (|2 2|
||| Beversel  [Temperature Sensiive Analysis
e Tt 57
Coeticent
ngth[1032 I'KF o Select Temp. Sensitive Analysis
Forr r|_vear

Pipe Data includes Heat Transfer'Coeff.

Temperature

— a0

Heat Loss

In Pipes

Superheated Steam Supply
100 psj @ 450 degrees F

5




Figure CF-24   Superheated Steam Distribution Model Details

Tabulated results are shown in Figure CF-25 and include the densities, viscosities, and temperatures, all which vary throughout the distribution system. Figures CF-26-27b show the pressure, temperature, and superheat for a load of 400 #/hr at each building. Figure CF-28 compares the building pressures for the saturated and superheated analyses.

[image: image512.png]FIPE  NODE  NODE FLOW TOS5  VELOCITY DENSITY FRICTION ARER  Heatoss Viscosity
wo. 8 2 (L8/HR)  (PSI)  (FI/S) (LB/CU FT) FACTOR RATIO (MBTU/hz) (£272/sec)
R 92 s99s.599  7.37 5788 T.21 0.015 0.091  142.53  3.19131E-07
10 g1 1200 0.32 sie2 0.21 0.015 0.032 0.17  2.23388E-07
s 12 800  0.12 20,99 0.21 0.016 0.021 0.0¢  2.432383E-07
ERTIE T 200 0.1 21,01 0.21 0.016 0.021 0.03  2.431624E-07
-2 918 sss.ses 0.22 22.42 0.22 0.018 0.023  15.36  2.784139E-07
15 17 4800 1.31 71,08 0.21 0.013 0.073  29.92  2.618906E-07
15 g-16 400 0.17 23.22 0.21 o.018 0.02¢ 618 2.5613025-07
317 35 4000 1.8 58,73 0.21 0.013 0.061  37.36  2.517983E-07
317 18 400 0.1 25,32 0.21 o0.018 0.02¢ 5.9 2.5161062-07
g-6  g-is  3ss.ses 0. 23.26 0.21 0.017 0.02¢ 0.03  2.442545E-07
Junceion Noae Toad Toaa  Enchalpy Pressuze  Pressure Density Sat. Temp. Act.Temp. Superfeat
o. Ticie (LB/HR) M-BTU/HR (STU/LB)  (PSIA) (PSIG) (18/£:"3) (Deg. F)  (Deg. F)  (Deg. F)
o-1 500 3se.98s se7.46  99.706  85.006 022 a6 327.6
310 o o o sesar  s0.241 0.21 324 324
11 o o o sse21  79.921 021 w38 s2s.e
912 o o o 5.5 5.8 021 3237 3237
913 o o o ss.362  73.662 021 a23.6  323.6
918 400 363.244  908.112  107.093  92.393 023 e 336 5.1
315 ] o o se.32  es.em2 021 3273 354 266
316 500 355.109  867.773  99.216  84.516 022 a2 s21.2
917 o o o ss.08 338 021 326.4 £ 6.5
g1 s00  3ss.e32  sse.se  97.962  83.262 022 3263 326.3
J-19 400  355.956 89.88  95.852  81.252 0.21 324,28 324.2




Figure CF-25  Superheated Steam Distribution Model – Tabulated Results
[image: image513.png]



Figure CF-26  Superheated Steam Distribution Model – Pressures (400 #/hr)

[image: image514.png]



Figure CF-27a  Superheated Steam Distribution  – Building Temps (400 #/hr)

[image: image515.png]



Figure CF-27b  Superheated Steam Distribution  – Superheat (400 #/hr)

[image: image516.png]



Saturated Steam

 [image: image517.png]



Superheated Steam

Figure CF-28  Comparing Models – Pressures for 400 #/hr

Pipe2016: Surge Demo Examples and Files
A demo for Pipe2016: Surge illustrates the use of this powerful transient analysis program. The surge demo has the following limitations: 10 pipes, 1 Pump, 1 SDO, 1 Active Valve, 1000 feet total length and 6 inch pipe diameter. The purpose of the surge demo is to illustrate a range of capabilities with limits imposed so the demo software will not be used commercially. Although Pipe2016: Surge can analyze large complex piping systems the demo consists of a single pipeline shown in Figure 1. A number of situations are modeled and analyzed:

1) Uncontrolled and controlled pump shutdown
2) Uncontrolled and controlled pump startup
3) Surge Protection (surge tank) for uncontrolled pump shutdown
4) Pump trip using full pump characteristics (pump file)
Data files for these examples are included in the program.  In the Open File window, click the Examples button and browse the 7 Surge Demos folder. The appropriate data file for the various situations will be noted.
[image: image518.png]---- 100 ft.----

elevaton -- 150

‘Butterfly Valve (Cv = 600)
120 11!

00 di HWC = 120

20 feet head

head flow
180 0
160 300

120 600




Figure 1 Pipeline Layout and Data
1) Uncontrolled and Controlled Pump Shutdown
demo shutdown no control.p2k
demo shutdown controlled.p2k
The pipeline layout and data is shown in Figure 1. The System Data is shown in Figure 2. Figure 3 shows the Pump and Active Valve data boxes. The main pipe lengths are scaled using the 100 foot grid lines. The wave speed for ductile iron (di) pipe is around 3900 ft/sec which is entered as the default.  The pump station pipes are just 5 feet long and are not shown to scale. It is generally recommended to model short pipes with a reduced wave speed so the computational time will not be excessively small.  Also a small amount of air entrainment in pump stations will considerably reduce wave speeds.

Once the data entry is completed the steady state analysis can be executed. The Pipe2016: Surge has the option to run just the initial steady state analysis as shown in Figure 3. It is recommended that the initial steady state analysis is always run and the results carefully checked and verified. The steady state results are shown in Figure 4 (Demo Shutdown No Control.P2K). The pressures and flow is displayed on the pipe system model. Also the pump operation shown in the detailed report is shown. A steady state flow of 577 gpm with the pump providing 123.6 feet of head is calculated as shown. The detailed report of the data and results should be carefully reviewed before doing a transient analysis.

[image: image519.png]Surge System Data
‘Specific Gravity [1
User Units | Units [Us gallons/min =~ ~

Fiction Equation [Hazen Williams |

Kinematic Viscosity [T |
Maximum # dTle,zo—
Accuacyoooot

Length Accuracy i

System Type |Surge -

Additional Data

Demand Calculation
[Fixed Demanas -]
ExtHead [ |
[ooroteatcutsteimtusion 7]
Leakage Factor

Wave Speed
Attribute used for pipes "Wave Speed”

Total Simuiation Time G0
Time Step Increment [

[wave speed

Default Wave Speed [3900





Figure 2  System Data
[image: image520.png]|Name[Pump-1—— |
[Pump -

[Elevation|100

——
SpRatio|1
—_——

|Pump Type _Hee
[Table E



[image: image521.png]



Pump Data

[image: image522.png]Name[AV-1
[Active Vabe  ~
fon| 100
Heabon] —__
Cv 100% 600 |

nit Ratiol T

abve Ty
Butterfly ~



 [image: image523.png]lcV Time 0



      [image: image524.png]Analysis Type

 Surge

 Surge with Force File

@ Etoady Statel

€ Debug




Active Valve Data and Steady State Analysis

Figure 3 Pump and Active Valve Data and Setup for Steady State Analysis 
[image: image525.png]



             Flow(gpm)  Hi(ft)    Ho(ft)   DH(ft)

Pump-1     576.72     19.84    143.33   123.6
Figure 4 Steady State Results

Once the steady state results are verified then data (Change Data) to describe the transient is entered as shown in Figure 5. This data is entered in the Change Data box for the associated element as shown on the left for the pump (Pump-1)   All Change Data can be reviewed using [image: image526.png]


 in the upper toolbars or Setup/Defaults-Change Pattern screen as shown in Figure 5. The first screens show the setup for an uncontrolled shutdown where the pump ramps down from full speed (1) to zero in 3 seconds starting 2 seconds into the simulation. The 2 second delay prior to the initiation of the transient is specified to assure that the system is holding the steady state conditions prior to the initiation of the transient. It s recommended that this procedure always be followed as an additional check on the model setup. The 2nd screen shows a controlled shutdown where the Butterfly Valve closes in 30 seconds and the pump speed ramps down in 10 seconds starting when the Butterfly valve is fully closed.

Results are shown in figure 6 which shows that the controlled shutdown (Demo Shutdown Controlled.P2K) produces a very small transient compared to the uncontrolled shutdown (Demo Shutdown No Control.P2K).

Figure 7 shows some screen shots from an animated profile module (Pipe2016). This module shows valve, pump, and surge protection devices actions and vapor cavity pocket formation and collapse.

[image: image527.png]Time/
Cons Value



 [image: image528.png]Changes for Pump-1

[rime

[Change

Valie

Speed ratio
speed ratio

1

o




Uncontrolled Pump Shut Down

[image: image529.png]Time/ Change
Change | Type
20
321
32/
425

oaex



 [image: image530.png]Changes for All Nodes

NoeName [Tme [Crange Vaue
) 2 o T
av-1 T2 ratio o
pump-1 2 specaraio 1
pump-1 2 specaraio 0





Controlled Valve and Pump Shut Down

Figure 5  Change Data and Change Pattern Screens for an Uncontrolled and Controlled Shutdown

[image: image531.png]oooooooooooooooooooooooooooooooooooo

1 W
T

eeeeeeee




Figure 6 Results for an Uncontrolled and Controlled Shutdown

[image: image532.png]siz

=4

sze

00z
(1) uoneAs|3

sl

st

sz

Distance (ft)




[image: image533.png]siz

=4

sze

00z
00 usnE ASIS

sl

st

sz

ook

Distance (f)




Figure 7 Animated Profile Displays of Results at beginning (top) and end (bottom) of the analysis
2) Uncontrolled and controlled pump startup
demo startup no control.p2k
demo startup controlled.p2k
Figure 8 shows the Change Pattern screens for an uncontrolled start up where the pump ramps up to full speed in 5 seconds. The screen on the right is for a controlled startup where the butterfly valve starts to open once the pump reaches full speed and opens in 20 seconds.  Figure 9 shows the results for the uncontrolled (Demo Startup No Control.P2K) and the controlled (Demo Startup Controlled.P2K) files and confirms that the controlled startup transient is much smaller.
[image: image534.png]Time/ |Change ~ New
Change| Type | Value
Pump-1 2s 0
Pump-1 7s 1

Node.



 [image: image535.png]Changes for Pump-1

[rime

Valie

Speed ratio
speed ratio




Startup No Control

[image: image536.png]Timel [Change| New
Node | hange| Type | Value
Pump-1 2s ]
Av-1 7 0
Pump-1 7/s 1
AVA 27 1



 [image: image537.png]Changes for All Nodes

[Node tame  [Time. [Change [Vae
Fump1 2 speed ratio 0
vt 7 rato o
Pump-1 7 speed ratio 1
av-t 2 rato 1




Startup Controlled
[image: image538.png]


                    [image: image539.png]



Figure 8 Change Pattern Screen for an Uncontrolled and Controlled Start Up
[image: image540.png]85
80

=75

2

=

o 70

5

265

©

2 80
55
50

10

20

30

Time (sec)

40

50

60




Figure 9 Results for an Uncontrolled and Controlled Start Up

3) Surge Protection (surge tank) for uncontrolled pump shutdown
demo surge tank.p2k
When a power outage occurs then an uncontrolled pump shutdown will occur (pump trip). When this happens, a surge protection device such as a surge tank may be required. This example illustrates modeling a surge tank for surge protection. The active valve is replaced by a surge tank (just select the active valve and select Closed Surge Tank from drop down list). The data for the surge tank is shown in Figure 10. Pipe2014: Surge has a tool to compute the resistance of the surge tank connection (Tools - Resistance Calculations/Connection to Tank). For a 6 inch connection a value of 1.0 is representative. The Surge Tank initial conditions (air volume, depth and tank diameter) are required input data. This surge tank is a 100 cubic foot (750 gallons) which is half full under the initial conditions. Figure 11 shows the pressure transient with and without the surge tank (Demo Surge Tank.P2K). To run the analysis w/o the surge tank just turn the tank OFF (ON/OFF button under Node Information).
[image: image541.png]


 [image: image542.png]Name[SDO-1
Closed Srg Tk~




 [image: image543.png]Device Data

Tank Vol 100

InGas Vol[50
ExpCon[12
Diameter[t
it Levlls



[image: image544.png]



Figure 10 Surge Tank Data
[image: image545.png]nnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnnn

2
Bl

100
90
80
70

@

eeeeeeee




Figure 11 Results for an Uncontrolled Shutdown with and w/o Surge Tank

4) Pump trip using full pump characteristics (pump file)
 demo pump trip.p2k

When modeling a power outage to a pump it is may be necessary to assume the ramp down time for the pump to go from full speed to zero. If the pump is equipped with a check valve which prevents reverse flow and turbining then making an assumption of 2-4 seconds will normally produce reasonable results. There is an option to utilize a Pump File which is based on four quadrant pump performance data. Thus, if the pump operates abnormally (turbining, etc.) a dynamic analysis can be carried out to determine the pump speed variation. A tool is available to determine which file to use (8 are available) and the appropriate inertia. It is recommended to use the operating pump head and flow to describe the pump when using the tool as shown in Figure 12. Using a pump head = 124 feet @ 576 gpm at 1000 rpm the tool suggests pump file 1 and an inertia around 10. Figure 12 shows the data boxes for defining a pump using a pump file. The Change Data can be used to specify a Pump Trip (at 2 seconds) as shown in Figure 12. Results presented in Figure 13 show that the transient using the pump file (Demo Pump Trip.P2K) is very similar to the one assuming a 3 second rundown. However, the use of a pump file to model a pump trip is recommended because the rundown time assumption is not required.
[image: image546.png]13 Pipe2000: Inertia - Specific Speed (CopyF

Unie e Engish ca

Flow Rate O (apml[576

Pump Head h (0128

Effciercyn (0t01) [75

Pump Power (HP) 2200
INERTIA (Ibft"2)

ity O Pumps 772

Smal g P [[55

Motorlnetia[g 57—

Comb netia old pumps) [1235
Comb.Ineta (mallpunes) 555
Calculated Inertia is WR"2 [NOT GD"2)
Specic Spoed (64587
Suggested Fump Fife [

Disclaimer Close




 [image: image547.png]Node Type  Pump - File

Name Pump-1
Elevation 100
Title

Parallel  Single
Check Valve
pon-Reopening Ch X
Bypass Line
CvTime 01

CV Resistance 0.1

Eficiency % 75

Speed Ratio 1
Grade —

File# (120) 1

Rated Head 124

Rated Flow 576
Rated Speed 1000

nertia 10




 

Pump Inertia Tool and File Pump Data (KYnetic)

[image: image548.png](Name|Pump-1
[Pump <]
[Elevation|100
——
SpRatio|1
—_—

Effcny%|78

|Pump Type _Hee
File E




[image: image549.png]Device Data

cvTimefod
CVRes[o1
File (1201
Rated Ha[124
Rated Fiu|576
Rated Spd[1000
Inertia[ 10

I™ Check Valve
¥ NonReopen CV




File Pump Data (Classic)

[image: image550.png]Cons Value

2 tTip



 [image: image551.png]Changes for Pump-1

[rime

Valie

[Change
trip

e




Pump Trip Change Data

Figure 12 Pump File Tool, Pump Data and Change Data

[image: image552.png]Pressure (psi)

100
90
80
70
60
50
40
30
20
10

Pump Trip - 4 Quadrant Characteristics

10

20

30 40
Time (sec)

50

60




[image: image553.png]Pressure (psi)

100
90
80
70
60
50
40
30
20
10

3 second shutdown - simulate pump trip

10

20

30 40
Time (sec)

50

60




Figure 13 Results for an Pump Trip and an Uncontrolled 3 second Shutdown
PAGE  
9

